## DATA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
Document No. | F/G | MODEL | Customer | Shunt (A) | Current (A) | Wave(mm.) | Wave(mm.) LOW | Wave(mm.) HIGH | Instan Low | Instan High | Percent of rate current | Trip time | Current setting | CT | Temp. (°C) | SW PCB unit | SW(V) | SW(A) | SW.P1 | Main nameplate No. | ELB nameplate No. | File N/P | File Label | Barcode | Terminal screw | Mounting screw | Phase separator | INSTRUCTION MANUAL | INSTRUCTION MANUAL 2 | INSTRUCTION MANUAL 3 | Name plate setting
255AF J | 33058755,A | SXK225 3P 225A (IVORY) | NAKAJO | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 140 | 5.00 - 25.00 min | 6.64 - 6.91 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058755A" | "1501-3235" | (M8X18) | (M4X40) | (PHS-4) | (S-21-21Q) | - | - | -
255AF J | 33058755,B | SXK225 3P 200A (IVORY) | NAKAJO | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155 | 5.00 - 20.00 min | 6.64 - 6.91 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058755B" | "1501-3234" | (M8X18) | (M4X40) | (PHS-4) | (S-21-21Q) | - | - | -
255AF J | 33058755,C | SXK225 3P 175A (IVORY) | NAKAJO | 1000200 | 2.41 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155.1 | 5.00 - 25.00 min | 5.80 - 6.04 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058755C" | "1501-3233" | (M8X18) | (M4X40) | (PHS-4) | (S-21-21Q) | - | - | -
255AF J | 33058755,D | SXK225 3P 150A (IVORY) | NAKAJO | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155.3 | 5.00 - 25.00 min | 4.92 - 5.12 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058755D" | "1501-3232" | (M8X18) | (M4X40) | (PHS-4) | (S-21-21Q) | - | - | -
255AF J | 33058755,E | SXK225 3P 125A (IVORY) | NAKAJO | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 160 | 5.00 - 25.00 min | 4.25 - 4.42 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058755E" | "1501-3231" | (M8X18) | (M4X40) | (PHS-4) | (S-21-21Q) | - | - | -
255AF J | 33058755,J | SXK225 2P 225A (IVORY) | NAKAJO | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 140 | 5.00 - 25.00 min | 6.64 - 6.91 A | 50 | 25 | - | - | - | - | 33058974B | - | "58974B" | "JP33058755J" | "1501-3225" | (M8X18) | (M4X40) | (PHS-4) | (S-21-21Q) | - | - | -
255AF J | 33058755,K | SXK225 2P 200A (IVORY) | NAKAJO | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155 | 5.00 - 20.00 min | 6.64 - 6.91 A | 50 | 25 | - | - | - | - | 33058974B | - | "58974B" | "JP33058755K" | "1501-3224" | (M8X18) | (M4X40) | (PHS-4) | (S-21-21Q) | - | - | -
255AF J | 33058755,L | SXK225 2P 175A (IVORY) | NAKAJO | 1000200 | 2.41 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155.1 | 5.00 - 25.00 min | 5.80 - 6.04 A | 50 | 25 | - | - | - | - | 33058974B | - | "58974B" | "JP33058755L" | "1501-3223" | (M8X18) | (M4X40) | (PHS-4) | (S-21-21Q) | - | - | -
255AF J | 33058755,M | SXK225 2P 150A (IVORY) | NAKAJO | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155.3 | 5.00 - 25.00 min | 4.92 - 5.12 A | 50 | 25 | - | - | - | - | 33058974B | - | "58974B" | "JP33058755M" | "1501-3222" | (M8X18) | (M4X40) | (PHS-4) | (S-21-21Q) | - | - | -
255AF J | 33058755,N | SXK225 2P 125A (IVORY) | NAKAJO | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 160 | 5.00 - 25.00 min | 4.25 - 4.42 A | 50 | 25 | - | - | - | - | 33058974B | - | "58974B" | "JP33058755N" | "1501-3221" | (M8X18) | (M4X40) | (PHS-4) | (S-21-21Q) | - | - | -
255AF ND J | 33058757,A | SXK225 3P 225A (IVORY) ND | NAKAJO | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 140 | 5.00 - 25.00 min | 6.64 - 6.91 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058757A" | "1501-3285" | - | - | - | - | - | - | -
255AF ND J | 33058757,C | SXK225 3P 175A (IVORY) ND | NAKAJO | 1000200 | 2.41 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155.1 | 5.00 - 25.00 min | 5.80 - 6.04 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058757C" | "1501-3283" | - | - | - | - | - | - | -
255AF ND J | 33058757,B | SXK225 3P 200A (IVORY) ND | NAKAJO | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155 | 5.00 - 20.00 min | 6.64 - 6.91 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058757B" | "1501-3284" | - | - | - | - | - | - | -
255AF ND J | 33058757,E | SXK225 3P 125A (IVORY) ND | NAKAJO | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 160 | 5.00 - 25.00 min | 4.25 - 4.42 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058757E" | "1501-3281" | - | - | - | - | - | - | -
255AF ND J | 33058757,D | SXK225 3P 150A (IVORY) ND | NAKAJO | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155.3 | 5.00 - 25.00 min | 4.92 - 5.12 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058757D" | "1501-3282" | - | - | - | - | - | - | -
255AF J | 33058756,A | SXK225 3P 225A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 140 | 5.00 - 25.00 min | 6.64 - 6.91 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058756A" | "1503-3235" | (M8X18) | (M4X40) | - | - | - | - | -
255AF J | 33058756,B | SXK225 3P 200A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155 | 5.00 - 20.00 min | 6.64 - 6.91 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058756B" | "1503-3234" | (M8X18) | (M4X40) | - | - | - | - | -
255AF J | 33058756,C | SXK225 3P 175A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 2.41 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155.1 | 5.00 - 25.00 min | 5.80 - 6.04 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058756C" | "1503-3233" | (M8X18) | (M4X40) | - | - | - | - | -
255AF J | 33058756,D | SXK225 3P 150A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155.3 | 5.00 - 25.00 min | 4.92 - 5.12 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058756D" | "1503-3232" | (M8X18) | (M4X40) | - | - | - | - | -
255AF J | 33058756,E | SXK225 3P 125A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 160 | 5.00 - 25.00 min | 4.25 - 4.42 A | 50 | 25 | - | - | - | - | 33058974A | - | "58974A" | "JP33058756E" | "1503-3231" | (M8X18) | (M4X40) | - | - | - | - | -
255AF J Nobarcode | 33058756,J | SXK225 2P 225A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 140 | 5.00 - 25.00 min | 6.64 - 6.91 A | 50 | 25 | - | - | - | - | 33058974B | - | "58974B" | "JP33058756J" | - | (M8X18) | (M4X40) | - | - | - | - | -
255AF J Nobarcode | 33058756,K | SXK225 2P 200A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155 | 5.00 - 20.00 min | 6.64 - 6.91 A | 50 | 25 | - | - | - | - | 33058974B | - | "58974B" | "JP33058756K" | - | (M8X18) | (M4X40) | - | - | - | - | -
255AF J Nobarcode | 33058756,L | SXK225 2P 175A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 2.41 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155.1 | 5.00 - 25.00 min | 5.80 - 6.04 A | 50 | 25 | - | - | - | - | 33058974B | - | "58974B" | "JP33058756L" | - | (M8X18) | (M4X40) | - | - | - | - | -
255AF J Nobarcode | 33058756,M | SXK225 2P 150A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155.3 | 5.00 - 25.00 min | 4.92 - 5.12 A | 50 | 25 | - | - | - | - | 33058974B | - | "58974B" | "JP33058756M" | - | (M8X18) | (M4X40) | - | - | - | - | -
255AF J Nobarcode | 33058756,N | SXK225 2P 125A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 160 | 5.00 - 25.00 min | 4.25 - 4.42 A | 50 | 25 | - | - | - | - | 33058974B | - | "58974B" | "JP33058756N" | - | (M8X18) | (M4X40) | - | - | - | - | -
| 33058755,Q | SXK225 2P NO RELAY (IVORY) | NAKAJO
| 33058755,G | SXK225 3P NO RELAY (IVORY) | NAKAJO
125AF DO | 3HTN001853TP,A | SXK32 3P 32A (Ivory) | PPK | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip | 144 | 5.30 - 10.30 min | 0.964 - 1.004 A | X50 | 25 | - | - | - | - | 3HTN001903A | - | "3HTN001903A" | "DO3HTN001853A" | - | (M5X14) | (M4X55) | (136-4) | (S-21-02J) | - | - |  | 125AF DO
125AF DO | 3HTN001854TP,S | SXK63 2P 32A (Ivory) | PPK | [12 empty] | - | - | - | - | 3HTN001915B | - | "3HTN001915B" | "DO3HTN001854S" | - | (M5X14) | (M4X55) | (136-4) | (S-21-02J) | - | - |  | 125AF DO
125AF DO | 3HTN001854TP,Q | SXK63 2P 50A (Ivory) | PPK | [12 empty] | - | - | - | - | 3HTN001915B | - | "3HTN001915B" | "DO3HTN001854Q" | - | (M5X14) | (M4X55) | (136-4) | (S-21-02J) | - | - |  | 125AF DO
125AF DO | 3HTN001854TP,E | SXK63 3P 32A (Ivory) | PPK | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip | 144 | 5.30 - 10.30 min | 0.964 - 1.004 A | X50 | 25 | - | - | - | - | 3HTN001915A | - | "3HTN001915A" | "DO3HTN001854E" | - | (M5X14) | (M4X55) | (136-4) | (S-21-02J) | - | - |  | 125AF DO
125AF DO | 3HTN001854TP,C | SXK63 3P 50A (Ivory) | PPK | 500100 | 4 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip | 141.7 | 4.30 - 9.00 min | 0.497 - 0.517 A | 150 | 25 | - | - | - | - | 3HTN001915A | - | "3HTN001915A" | "DO3HTN001854C" | - | (M5X14) | (M4X55) | (136-4) | (S-21-02J) | - | - |  | 125AF DO
125AF DO | 3HTN001855TP,A | FXK63 3P 63A (Ivory) | PPK | 500100 | 5.04 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip | 147.4 | 5.00 - 10.30 min | 0.647 - 0.674 A | 150 | 25 | - | - | - | - | 3HTN001915C | - | "3HTN001915C" | "DO3HTN001855A" | - | (M8X14) | (M4X55) | (PHS-4) | (S-21-02J) | - | - |  | 125AF DO
125AF DO | 3HTN001856TP,D | SXK125-SA 3P 75A (Ivory) | PPK | 500100 | 5 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip | 143 | 4.30 - 11.00 min | 1.237 - 1.287 A | 150 | 25 | - | - | - | - | 3HTN001915E | - | "3HTN001915E" | "DO3HTN001856D" | - | (M8X14) | (M4X55) | (PHS-4) | (S-21-02J) | - | - |  | 125AF DO
125AF DO | 3HTN001858TP,D | FXK125-S 3P 75A (Ivory) | PPK | 500100 | 3 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip | 148 | 8.00 - 14.00 min | 0.787 - 0.819 A | 150 | 25 | - | - | - | - | 3HTN001919A | - | "3HTN001919A" | "DO3HTN001858D" | - | (M8X14) | (M4X55) | (PHS-4) | (S-21-02J) | - | - |  | 125AF DO
125AF DO | 3HTN001858TP,B | FXK125-S 3P 100A (Ivory) | PPK | 500100 | 4 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip | 148 | 8.00 - 13.00 min | 1.047 - 1.090 A | 150 | 25 | - | - | - | - | 3HTN001919A | - | "3HTN001919A" | "DO3HTN001858B" | - | (M8X14) | (M4X55) | (PHS-4) | (S-21-02J) | - | - |  | 125AF DO
125AF DO | 3HTN001860TP,A | FXK125-H 3P 125A (Ivory) | PPK | 500100 | 5 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip | 145 | 8.00 - 14.00 min | 1.273 - 1.325 A | 150 | 25 | - | - | - | - | 3HTN001919C | - | "3HTN001919C" | "DO3HTN001860A" | - | (M8X14) | (M4X55) | (PHS-4) | (S-21-02J) | - | - |  | 125AF DO
125AF DO | 3HTN001860TP,B | FXK125-H 3P 100A (Ivory) | PPK | 500100 | 4 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip | 148 | 8.00 - 13.00 min | 1.047 - 1.090 A | 150 | 25 | - | - | - | - | 3HTN001919C | - | "3HTN001919C" | "DO3HTN001860B" | - | (M8X14) | (M4X55) | (PHS-4) | (S-21-02J) | - | - |  | 125AF DO
255AF DO | 3HTN001864TP,E | SXK225 3P 125A (Ivory) | PPK | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 160 | 5.00 - 25.00 min | 4.250 - 4.420 A | 50 | 25 | - | - | - | - | 3HTN001943A | - | "3HTN001943A" | "DO3HTN001864E" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
255AF DO | 3HTN001864TP,B | SXK225 3P 200A (Ivory) | PPK | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155 | 5.00 - 20.00 min | 6.640 - 6.910 A | 50 | 25 | - | - | - | - | 3HTN001943A | - | "3HTN001943A" | "DO3HTN001864B" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
255AF DO | 3HTN001864TP,A | SXK225 3P 225A (Ivory) | PPK | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 140 | 5.00 - 25.00 min | 6.640 - 6.910 A | 50 | 25 | - | - | - | - | 3HTN001943A | - | "3HTN001943A" | "DO3HTN001864A" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
255AF DO | 3HTN001864TP,D | SXK225 3P 150A (Ivory) | PPK | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip | 155.3 | 5.00 - 25.00 min | 4.920 - 5.120 A | 50 | 25 | - | - | - | - | 3HTN001943A | - | "3HTN001943A" | "DO3HTN001864D" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
255AF DO | 3HTN001870TP,G | FXK250-H 3P 125A (Ivory) | PPK | 1000200 | 1.88 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip | 148 | 10.24 - 17.00 min | 3.89 - 4.05 A | 50 | 25 | - | - | - | - | 3HTN001944A | - | "3HTN001944A" | "DO3HTN001870G" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
255AF DO | 3HTN001870TP,F | FXK250-H 3P 150A (Ivory) | PPK | 1000200 | 2.25 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip | 146 | 9.30 - 16.06 min | 4.59 - 4.78 A | 50 | 25 | - | - | - | - | 3HTN001944A | - | "3HTN001944A" | "DO3HTN001870F" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
255AF DO | 3HTN001870TP,C | FXK250-H 3P 200A (Ivory) | PPK | 1000200 | 3 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip | 144 | 7.54 - 12.06 min | 6.03 - 6.28 A | 50 | 25 | - | - | - | - | 3HTN001944A | - | "3HTN001944A" | "DO3HTN001870C" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
255AF DO | 3HTN001870TP,B | FXK250-H 3P 225A (Ivory) | PPK | 1000200 | 3.38 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip | 147 | 6.00 - 9.30 min | 6.97 - 7.25 A | 50 | 25 | - | - | - | - | 3HTN001944A | - | "3HTN001944A" | "DO3HTN001870B" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
255AF DO | 3HTN001868TP,G | FXK250-S 3P 125A (Ivory) | PPK | 1000200 | 1.88 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip | 148 | 10.24 - 17.00 min | 3.89 - 4.05 A | 50 | 25 | - | - | - | - | 3HTN001944C | - | "3HTN001944C" | "DO3HTN001868G" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
255AF DO | 3HTN001868TP,F | FXK250-S 3P 150A (Ivory) | PPK | 1000200 | 2.25 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip | 146 | 9.30 - 16.06 min | 4.59 - 4.78 A | 50 | 25 | - | - | - | - | 3HTN001944C | - | "3HTN001944C" | "DO3HTN001868F" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
255AF DO | 3HTN001868TP,B | FXK250-S 3P 225A (Ivory) | PPK | 1000200 | 3.38 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip | 147 | 6.00 - 9.30 min | 6.97 - 7.25 A | 50 | 25 | - | - | - | - | 3HTN001944C | - | "3HTN001944C" | "DO3HTN001868B" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
255AF DO | 3HTN001868TP,A | FXK250-S 3P 250A (Ivory) | PPK | 1000200 | 3.75 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip | 144 | 7.06 - 9.30 min | 3.78 - 3.94 A | 100 | 25 | - | - | - | - | 3HTN001944C | - | "3HTN001944C" | "DO3HTN001868A" | - | (M8X18) | (M4X40) | (PHS-4) | (S-21-02J) | - | - |  | 255AF DO
F-630F DO | 3HTN001883TP,A | F-630F 3P 630A (Ivory) | PPK | 1000200 | 3.15 | 5 | 10 | 25 | Lower 200% ∼ 100ms No-Trip | High 500% ∼ 60ms Trip | 129 | 15.00 - 20.00 min | 6.65 - 6.92 A | 130 | 25 | - | - | - | - | 3HTN001941C | - | "3HTN001941C" | "DO3HTN001883A" | - | (M12X40) | (M6X45) | (PHS-5) | (S-21-02J) | - | - |  | F-630F DO
FX400 DO | 3HTN001878TP,A | FX400 3P 400A (Ivory) | PPK | - | - | - | - | - | - | - | 400 | 19 - 30 sec | 720 - 880 A | - | - | 8 | 2.6 | 900 | 400 | 3HTN001940C | - | "3HTN001940C" | "DO3HTN001878A" | - | (M10X30) | (M6X45) | (PHS-5B) | (S-21-02J) | (S-21-22C) | - | 33030290-1 | FX400 DO
F-1000C DO | 3HTN001897TP,A | F-1000C 3P 1000A (Ivory) | PPK | - | - | - | - | - | - | - | - | 1.00 - 2.00 min | - | - | - | - | - | - | - | 3HTN001950E | - | "3HTN001950E" | "DO3HTN001897A" | - | (M12X50) | (M8X40) | (PHS-16) | (S-21-02J) | (S-21-22C) | (33024374) |  | F-1000C DO
400AF DO | 3HTN001874TP,A | S-400S 3P 400A (Ivory) | PPK | 1000200 | 4.5 | 5 | 20 | 24.4 | Lower 900% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip | 120 | 14.00 - 28.00 min | 5.10 - 5.31 min | 100 | 25 | - | - | - | - | 3HTN001929A | - | "3HTN001929A" | "DO3HTN001874A" | - | (M10X30) | (M6X45) | (PHS-5B) | (S-21-02J) | - | - |  | 400AF DO
400AF DO | 3HTN001874TP,B | S-400S 3P 350A (Ivory) | PPK | 1000200 | 4.16 | 5 | 20 | 23.2 | Lower 900% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip | 120 | 13.00 - 25.00 min | 8.98 - 9.35 min | 50 | 25 | - | - | - | - | 3HTN001929A | - | "3HTN001929A" | "DO3HTN001874B" | - | (M10X30) | (M6X45) | (PHS-5B) | (S-21-02J) | - | - |  | 400AF DO
400AF DO | 3HTN001874TP,C | S-400S 3P 300A (Ivory) | PPK | 1000200 | 3.75 | 5 | 20 | 24 | Lower 1000% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip | 125 | 14.00 - 21.00 min | 8.08 - 8.41 A | 50 | 25 | - | - | - | - | 3HTN001929A | - | "3HTN001929A" | "DO3HTN001874C" | - | (M10X30) | (M6X45) | (PHS-5B) | (S-21-02J) | - | - |  | 400AF DO
400AF DO | 3HTN001876TP,C | F-400R 3P 300A (Ivory) | PPK | 1000200 | 3.75 | 5 | 20 | 24 | Lower 1000% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip | 125 | 14.00 - 21.00 min | 8.08 - 8.41 A | 50 | 25 | - | - | - | - | 3HTN001929C | - | "3HTN001929C" | "DO3HTN001876C" | - | (M10X30) | (M6X45) | (PHS-5B) | (S-21-02J) | - | - |  | 400AF DO
400AF DO | 3HTN001876TP,B | F-400R 3P 350A (Ivory) | PPK | 1000200 | 4.16 | 5 | 20 | 23.2 | Lower 900% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip | 120 | 13.00 - 25.00 min | 8.98 - 9.35 min | 50 | 25 | - | - | - | - | 3HTN001929C | - | "3HTN001929C" | "DO3HTN001876B" | - | (M10X30) | (M6X45) | (PHS-5B) | (S-21-02J) | - | - |  | 400AF DO
400AF DO | 3HTN001876TP,A | F-400R 3P 400A (Ivory) | PPK | 1000200 | 4.5 | 5 | 20 | 24.4 | Lower 900% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip | 120 | 14.00 - 28.00 min | 5.10 - 5.31 min | 100 | 25 | - | - | - | - | 3HTN001929C | - | "3HTN001929C" | "DO3HTN001876A" | - | (M10X30) | (M6X45) | (PHS-5B) | (S-21-02J) | - | - |  | 400AF DO
FX400 DO | 3HTN001875TP,A | SX400 3P 400A (Ivory) | PPK | - | - | - | - | - | - | - | 400 | 19 - 30 sec | 720 - 880 A | - | - | 8 | 2.6 | 900 | 400 | 3HTN001940A | - | "3HTN001940A" | "DO3HTN001875A" | - | (M10X30) | (M6X45) | (PHS-5B) | (S-21-02J) | (S-21-22C) | - | 33030290-1 | FX400 DO
800AF DO NOBAG | 3HTN001890TP,A | F-800R 3P 800A (Ivory) | PPK | 1000200 | 4 | 5 | 10 | 25 | Lower 200% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip | 125 | 14.00 - 18.00 min | 8.18 - 8.51 A | 130 | 25 | - | - | - | - | 3HTN001941G | - | "3HTN001941G" | "DO3HTN001890A" | - | (M12X40) | (M6X45) | (PHS-5) | (S-21-02J) | - | - |  | 800AF DO NOBAG
FX600 DO | 3HTN001885TP,B | FX600 3P 600A (Ivory) | PPK | - | - | - | - | - | - | - | 400 | 19 - 30 sec | 1,080 - 1320 A | - | - | 6 | 4 | 1800 | 600AF | 3HTN001947B | - | "3HTN001947B" | "DO3HTN001885B" | - | (M12X40) | (M6X45) | (PHS-5) | (S-21-02J) | (S-21-22C) | - | 33030322-1 | FX600 DO
125AF DO | 3HTN001857TP,H | FXK125-SA 3P 40A (Ivory) | PPK | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip | 146.2 | 4.30 - 9.00 min | 1.235 - 1.286 A | 50 | 25 | - | - | - | - | 3HTN001915G | - | "3HTN001915G" | "DO3HTN001857H" | - | (M5X14) | (M4X55) | (136-4) | (S-21-02J) | - | - |  | 125AF DO
125AF DO | 3HTN001858TP,J | FXK125-S 3P 32A (Ivory) | PPK | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip | 148 | 7.00 - 18.00 min | 1.639 - 1.706 A | 30 | 25 | - | - | - | - | 3HTN001919A | - | "3HTN001919A" | "DO3HTN001858J" | - | (M6X14) | (M4X55) | (136-4) | (S-21-02J) | - | - |  | 125AF DO
| 33058748,D | SXK125-C 3P 60A ND (Ivory) | NAKAJO | 500100 | 4.8 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip | 147.4 | 5.00 - 13.00 min | 0.621 - 0.647 A | 150 | 25 |  |  |  |  | 33058949D | - | [10 empty] | 2481
| 33058745,D | SXK125-C 3P 60A (IVORY) | NAKAJO | 500100 | 4.8 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.00 - 13.00 min | 0.621 - 0.647 A | 150 | 25 |  |  |  |  | 33058949D | [11 empty] | 2480
| 33046717TS,D | RXK250-H 3P 175A 30mA AC200-440V (Light Gray) | NAKAJO | 1000200 | 2.14 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 9.00 - 15.00 min | 5.18 - 5.39 A | 50 | 25 |  |  |  |  | 33047693C | [11 empty] | 2476
| 33058785,N | EXK125-C 3P 125A 100.200.500mA (Ivory) | NAKAJO | 500100 | 5 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 10.30 - 20.00 min | 1.123 - 1.168 A | 150 | 25 |  |  |  |  | 33058956K | [11 empty] | 2475
| 33058818,N | EXKN125-C 3P AC100/200V 125A 100.200.500mA N (Ivory) | NAKAJO | 500100 | 5 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 10.50 - 20.00 min | 1.123 - 1.168 A | 150 | 25 |  |  |  |  | 33058962K | [11 empty] | 2471
| 33058815,A | SXKN125-C 3P (AC100/200V) 125A (IVORY) | NAKAJO | 500100 | 5 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 10.50 - 20.00 min | 1.124 - 1.170 A | 150 | 25 |  |  |  |  | 33058953A | [11 empty] | 2473
| 33058725,V | FXK125-H 2P 20A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.00 - 22.00 min | 0.940 - 0.978 A | 30 | 25 |  |  |  |  | 33058966H | [11 empty] | 2469
| 33058752,W | FXK125-H 2P 15A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.00 - 11.00 min | 0.695 - 0.723 A | 30 | 25 |  |  |  |  | 33058966J | [11 empty] | 2468
| 33047237,B | S-50SB 3P 40A SHT-AUX (DC12V) (New Jis) | NAKAJO | 500100 | 3.2 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 5.09 min | 1.57 - 1.62 A | 50 | 25 |  |  |  |  | 33046170H | [11 empty] | 2360
| 33047237,P | S-50SB 2P 40A SHT-AUX (DC12V) (New JIS) | NAKAJO | 500100 | 3.2 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 5.09 min | 1.57 - 1.62 A | 50 | 25 |  |  |  |  | 33046171H | [11 empty] | 2359
| 33047237,C | S-50SB 3P 30A SHT-AUX (DC12V) (New JIS) | NAKAJO | 500100 | 2.4 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 2.31 min | 1.18 - 1.22 A | 50 | 25 |  |  |  |  | 33046170J | [11 empty] | 2352
| 33047237,Q | S-50SB 2P 30A SHT-AUX (DC12V) (New JIS) | NAKAJO | 500100 | 2.4 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 2.31 min | 1.18 - 1.22 A | 50 | 25 |  |  |  |  | 33046171J | [11 empty] | 2351
| 33047240,L | S-225SB 2P 175A SHT-AUX (DC12V) (New JIS) | NAKAJO | 1000200 | 2.41 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 25 min | 5.80 - 6.04 A | 50 | 25 |  |  |  |  | 33043135B | [11 empty] | 2162
| 33047240,C | S-225SB 3P 175A SHT-AUX (DC12V) (New JIS) | NAKAJO | 1000200 | 2.41 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 25 min | 5.80 - 6.04 A | 50 | 25 |  |  |  |  | 33043135A | [11 empty] | 2157
| 33047237,A | S-50SB 3P 50A SHT-AUX (DC12V) (New JIS) | NAKAJO | 500100 | 4 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 5.09 min | 0.65 - 0.68 A | 150 | 25 |  |  |  |  | 33046170G | [11 empty] | 2018
| 33047239,P | S-100SB 2P 75A SHT-AUX DC12V | NAKAJO | 500100 | 3 | 5 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 5.09 min | 0.98 - 1.02 A | 150 | 25 |  |  |  |  | 33046198B | [11 empty] | 1949
| 33058758,W | FXK250-S 3P 250A (Ivory) ND | NAKAJO | 1000200 | 3.75 | 5 | 20 | 26.7 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 7.10 - 9.50 min | 3.78 - 3.94 A | 100 | 25 |  |  |  |  | 33058978C | [11 empty] | 1948
| 330430580TS,C | F-630F 3P 500A (Light Gray) | Sangchai | 1000200 | 2.5 | 5 | 10 | 25 | Lower 200% ∼ 100ms No-Trip | High 500% ∼ 60ms Trip |  | 14.00 - 18.00 min | 7.40 - 7.70 A | 90 | 25 |  |  |  |  | 3HTN001694D | [11 empty] | 1947
| 330430580TP,C | F-630F 3P 500A (Light Gray) | PPK | 1000200 | 2.5 | 5 | 10 | 25 | Lower 200% ∼ 100ms No-Trip | High 500% ∼ 60ms Trip |  | 14.00 - 18.00 min | 7.40 - 7.70 A | 90 | 25 |  |  |  |  | 3HTN001694D | [11 empty] | 1946
| 330430580TP,B | F-630F 3P 600A (Light Gray) | PPK | 1000200 | 3 | 5 | 10 | 25 | Lower 200% ∼ 100ms No-Trip | High 500% ∼ 60ms Trip |  | 15.00 - 20.00 min | 6.65 - 6.92 A | 130 | 25 |  |  |  |  | 3HTN001694D | [11 empty] | 1945
| 330430580TP,A | F-630F 3P 630A (Light Gray) | Domestic | 1000200 | 3.15 | 5 | 10 | 25 | Lower 200% ∼ 100ms No-Trip | High 500% ∼ 60ms Trip |  | 15.00 - 20.00 min | 6.65 - 6.92 A | 90 | 25 |  |  |  |  | 3HTN001694D | [11 empty] | 1944
| 33058776,N | FX800 3P 800A (Ivory) | NAKAJO | - | - | - | - | - | - | - |  | 19 - 30 sec | 1440 - 1760 A | - | - | - | - | - | - | 33058996G | [11 empty] | 1943
| 33058776,P | FX800 3P 800A Y (Ivory) | NAKAJO | - | - | - | - | - | - | - |  | 19 - 30 sec | 1440 - 1760 A | - | - | - | - | - | - | 33058996G | [11 empty] | 1942
| 33058787,N | RXK125-SA 3P 125A AC 100-440V 100.200.500mA (Ivory) | NAKAJO | 500100 | 5 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 10.50 - 20.00 min | 1.123 - 1.168 A | 150 | 25 |  |  |  |  | 33058954K | [11 empty] | 1941
| 33058767,G | F-400FB 2P 300A (IVORY) | NAKAJO | 1000200 | 3.75 | 5 | 20 | 24 | Lower 1,000% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip |  | 14.00 - 21.00 min | 8.08 - 8.41 A | 50 | 25 |  |  |  |  | 33058984D | [11 empty] | 1940
| 33058745,F | SXK125-C 3P 40A (Ivory) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 4.50 - 9.00 min | 1.235 - 1.285 A | 50 | 25 |  |  |  |  | 33058949F | [11 empty] | 1939
| 33058776,J | SX800 3P 800A (Ivory) | NAKAJO | [8 empty] | 19 - 30 sec | 1440 - 1760 A | [6 empty] | 33058996C | [11 empty] | 1938
| 33058761,E | FXE225-H 3P 125A (Ivory) | NAKAJO | 1000200 | 3.4 | 5 | 20 | 30 | Lower 2,720% ∼ 100ms No-Trip | High 4,080% ∼ 60ms Trip |  | 30 - 65 sec | 2.45 - 2.55 A | 100 | 25 |  |  |  |  | 33058981A | [11 empty] | 1937
| 33058758,D | FXK250-S 3P 175A (Ivory) | NAKAJO | 1000200 | 2.63 | 5 | 20 | 26.7 | Lower 1,000% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 8.20 - 15.2 min | 5.18 - 5.39 A | 50 | 25 |  |  |  |  | 33058978C | [11 empty] | 1936
| 33061296,B | FXK125-H 3P 100A Reversible Connection Type (Ivory) | NAKAJO | 500100 | 4 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 8.00 - 13.00 min | 1.047 - 1.090 A | 150 | 25 |  |  |  |  | 33061295B | [11 empty] | 1935
| 33058776,F | FX600 3P 600A Y (Ivory) | NAKAJO | [8 empty] | 19 - 30 sec | 1080 - 1320 A | [6 empty] | 33058996E | [11 empty] | 1934
| 33058745,H | SXK125-C 3P 20A (Ivory) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 6.00 - 13.00 min | 0.586 - 0.610 A | 50 | 25 |  |  |  |  | 33058949H | [11 empty] | 1878
| 33058758,B | FXK250-S 3P 225A (IVORY) | NAKAJO | 1000200 | 3.38 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 6.00 -9.50 min | 6.97 - 7.25 A | 50 | 25 |  |  |  |  | 33058978C | [11 empty] | 1877
| 33058758,E | FXK250-S 3P 150A (IVORY) | NAKAJO | 1000200 | 2.25 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 9.50 - 16.10 min | 4.59 - 4.78 A | 50 | 25 |  |  |  |  | 33058978C | [11 empty] | 1876
| 33058767,E | F-400FB 2P 400A (IVORY) | NAKAJO | 1000200 | 4.5 | 5 | 20 | 24.4 | Lower 900% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip |  | 14.00 - 28.00 min | 5.10 - 5.31 A | 100 | 25 |  |  |  |  | 33058984D | [11 empty] | 1875
| 33058771,P | S-800S 3P 700A (IVORY) | NAKAJO | 1000200 | 3.5 | 5 | 10 | 25 | Lower 200% ∼ 100ms No-Trip | High 500% ∼ 60ms Trip |  | 14.00 - 21.00 min | 7.15 - 7.45 A | 130 | 25 |  |  |  |  | 33058998C | [11 empty] | 1874
| 33058751,W | FXK125-S 2P 15A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.00 - 11.00 min | 0.694 - 0.723 A | 30 | 25 |  |  |  |  | 33058966V | [11 empty] | 1873
| 33058751,V | FXK125-S 2P 20A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.00 - 20.00 min | 0.939 - 0.977 A | 30 | 25 |  |  |  |  | 33058966U | [11 empty] | 1872
| 33058751,U | FXK125-S 2P 30A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 4.00 - 11.00 min | 1.461 - 1.520 A | 30 | 25 |  |  |  |  | 33058966T | [11 empty] | 1871
| 33058751,T | FXK125-S 2P 40A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.00 - 14.00 min | 0.405 - 0.422 A | 150 | 25 |  |  |  |  | 33058966S | [11 empty] | 1859
| 33058751,R | FXK125-S 2P 60A (IVORY) | NAKAJO | 500100 | 4.8 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.30 - 13.00 min | 0.626 - 0.652 A | 150 | 25 |  |  |  |  | 33058966Q | [11 empty] | 1858
| 33058751,Q | FXK125-S 2P 75A (IVORY) | NAKAJO | 500100 | 3 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.00 - 10.00 min | 0.787 - 0.819 A | 150 | 25 |  |  |  |  | 33058966P | [11 empty] | 1857
| 33058751,P | FXK125-S 2P 100A (IVORY) | NAKAJO | 500100 | 4 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 7.00 - 11.00 min | 1.047 - 1.090 A | 150 | 25 |  |  |  |  | 33058966N | [11 empty] | 1856
| 33058751,N | FXK125-S 2P 125A (IVORY) | NAKAJO | 500100 | 5 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 9.00 - 16.00 min | 1.273 - 1.325 A | 150 | 25 |  |  |  |  | 33058966M | [11 empty] | 1855
| 33058750,P | FXK60-H 2P 50A (IVORY) | NAKAJO | 500100 | 4 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.00 - 9.00 min | 0.518 - 0.539 A | 150 | 25 |  |  |  |  | 33058968B | [11 empty] | 1853
| 33058750,N | FXK60-H 2P 60A (IVORY) | NAKAJO | 500100 | 4.8 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.30 - 13.00 min | 0.626 - 0.652 A | 150 | 25 |  |  |  |  | 33058968A | [11 empty] | 1854
| 33058750,Q | FXK0-H 2P 40A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.00 - 14.00 min | 0.405 - 0.421 A | 150 | 25 |  |  |  |  | 33058968C | [11 empty] | 1852
| 33058767,J | F-400FB 4P 400A (IVORY) | NAKAJO | 1000200 | 4.5 | 5 | 20 | 24.4 | Lower 900% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip |  | 14.00 - 28.00 min | 5.10 - 5.31 A | 100 | 25 |  |  |  |  | 33058984E | [11 empty] | 1832
| 33058767,K | F-400FB 4P 350A (IVORY) | NAKAJO | 1000200 | 4.16 | 5 | 20 | 23.2 | Lower 950% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip |  | 13.00 - 25.00 min | 8.98 - 9.35 A | 50 | 25 |  |  |  |  | 33058984E | [11 empty] | 1831
| 33058767,L | F-400FB 4P 300A (IVORY) | NAKAJO | 1000200 | 3.75 | 5 | 20 | 24 | Lower 1,000% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip |  | 14.00 - 21.00 min | 8.08 - 8.41 A | 50 | 25 |  |  |  |  | 33058984E | [11 empty] | 1830
| 33058767,M | F-400FB 4P 250A (IVORY) | NAKAJO | 1000200 | 3.13 | 5 | 20 | 24 | Lower 1,000% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip |  | 15.00 - 26.00 min | 6.64 - 6.91 A | 50 | 25 |  |  |  |  | 33058984E | [11 empty] | 1829
| 33047127TP,M | EXK225 3P 150A 200-440 100.200.500mA 0.1sec | HAS/THAI | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 6.00 - 12.00 min | 4.92 - 5.12 A | 50 | 25 |  |  |  |  | 33047691A | [11 empty] | 1827
| 33058754,A | FXK50-HU 3P 10A (IVORY) | NAKAJO | 100(X20) | 4 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 2.00 min | 1.31 - 1.36 A | 15 | 25 |  |  |  |  | 33058969A | [11 empty] | 1826
| 33058754,C | FXK50-HU 3P 3A (IVORY) | NAKAJO | 100(X20) | 1.2 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 2.00 min | 1.31 - 1.36 A | 15 | 25 |  |  |  |  | 33058969A | [11 empty] | 1825
| 33058754,G | FXK50-HU 2P 3A (IVORY) | NAKAJO | 100(X20) | 1.2 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 2.00 min | 1.31 - 1.36 A | 15 | 25 |  |  |  |  | 33058970C | [11 empty] | 1824
| 33058745,G | SXK125-C 3P 30A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 4.00 - 10.00 min | 0.908 - 0.946 A | 50 | 25 |  |  |  |  | 33058949G | [11 empty] | 1823
| 33058827,J | F-225KC 4P 225A (IVORY) | NAKAJO | 1000200 | 3.38 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 8.00 - 15.00 min | 6.41 - 6.67 A | 50 | 25 |  |  |  |  | 33058985B | [11 empty] | 1822
| 33058827,K | F-225KC 4P 200A (IVORY) | NAKAJO | 1000200 | 3 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 7.00 - 14.00 min | 5.89 - 6.13 A | 50 | 25 |  |  |  |  | 33058985B | [11 empty] | 1821
| 33058827,M | F-225KC 4P 150A (IVORY) | NAKAJO | 1000200 | 2.25 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,380% ∼ 60ms Trip |  | 10.00 - 20.00 min | 4.40 - 4.58 A | 50 | 25 |  |  |  |  | 33058985B | [11 empty] | 1820
| 33058816,E | SN225 3P AC100/200V 125A (IVORY) | NAKAJO | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 25.00 min | 4.25 - 4.42 A | 50 | 25 |  |  |  |  | 33058977A | [11 empty] | 1819
| 33058816,D | SN225 3P AC100/200V 150A (IVORY) | NAKAJO | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 25.00 min | 4.92 - 5.12 A | 50 | 25 |  |  |  |  | 33058977A | [11 empty] | 1818
| 33058816,C | SN225 3P AC100/200V 175A (IVORY) | NAKAJO | 1000200 | 2.41 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 25.00 min | 5.80 - 6.04 A | 50 | 25 |  |  |  |  | 33058977A | [11 empty] | 1817
| 33058816,B | SN225 3P AC100/200V 200A (IVORY) | NAKAJO | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 20.00 min | 6.64 - 6.91 A | 50 | 25 |  |  |  |  | 33058977A | [11 empty] | 1816
| 33058747,J | FXK125-SA 3P 15A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 7.30 - 13.00 min | 0.449 - 0.467 A | 50 | 25 |  |  |  |  | 33058948J | [11 empty] | 1815
| 33058747,H | FXK125-SA 3P 20A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 6.00 - 13.00 min | 0.586 - 0.610 A | 50 | 25 |  |  |  |  | 33058948H | [11 empty] | 1814
| 33058747,G | FXK125-SA 3P 30A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.00 - 10.00 min | 0.494 - 0.514 A | 150 | 25 |  |  |  |  | 33058948G | [11 empty] | 1813
| 33058747,F | FXK125-SA 3P 40A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 4.30 - 9.00 min | 1.235 - 1.286 A | 50 | 25 |  |  |  |  | 33058948F | [11 empty] | 1812
| 33058747,E | FXK125-SA 3P 50A (IVORY) | NAKAJO | 500100 | 4 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.00 - 11.00 min | 0.494 - 0.514 A | 150 | 25 |  |  |  |  | 33058948E | [11 empty] | 1811
| 33058747,D | FXK125-SA 3P 60A (IVORY) | NAKAJO | 500100 | 4.8 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.00 - 13.00 min | 0.621 - 0.647 A | 150 | 25 |  |  |  |  | 33058948D | [11 empty] | 1810
| 33058747,A | FXK125-SA 3P 125A (IVORY) | NAKAJO | 500100 | 5 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 4.30 - 11.00 min | 1.237 - 1.287 A | 150 | 25 |  |  |  |  | 33058948A | [11 empty] | 1809
| 33058747,W | FXK125-SA 2P 15A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.00 - 8.00 min | 0.456 - 0.475 A | 50 | 25 |  |  |  |  | 33058948W | [11 empty] | 1801
| 33058747,V | FXK125-SA 2P 20A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 6.30 - 12.00 min | 0.574 - 0.597 A | 50 | 25 |  |  |  |  | 33058948V | [11 empty] | 1800
| 33058747,U | FXK125-SA 2P 30A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 4.00 - 8.00 min | 0.907 - 0.944 A | 50 | 25 |  |  |  |  | 33058948U | [11 empty] | 1799
| 33058747,T | FXK125-SA 2P 40A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.00 - 13.00 min | 1.173 - 1.221 A | 50 | 25 |  |  |  |  | 33058948T | [11 empty] | 1798
| 33058747,S | FXK125-SA 2P 50A (IVORY) | NAKAJO | 500100 | 4 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 4.30 - 9.00 min | 0.497 - 0.517 A | 150 | 25 |  |  |  |  | 33058948S | [11 empty] | 1797
| 33058747,R | FXK125-SA 2P 60A (IVORY) | NAKAJO | 500100 | 4.8 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 7.30 - 15.00 min | 0.619 - 0.644 A | 150 | 25 |  |  |  |  | 33058948R | [11 empty] | 1796
| 33058747,Q | FXK125-SA 2P 75A (IVORY) | NAKAJO | 500100 | 3 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 4.30 - 10.30 min | 0.761 - 0.792 A | 150 | 25 |  |  |  |  | 33058948Q | [11 empty] | 1795
| 33058747,P | FXK125-SA 2P 100A (IVORY) | NAKAJO | 500100 | 4 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.30 - 11.00 min | 1.015 - 1.056 A | 150 | 25 |  |  |  |  | 33058948P | [11 empty] | 1794
| 33047237,N | S-50SB 2P 50A SHT-AUX (DC12V) (New JIS) | NAKAJO | 500100 | 4 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 5.09 min | 0.65 - 0.68 A | 150 | 25 |  |  |  |  | 33046171G | [11 empty] | 1784
| 33058816,A | SN225 3P AC100/200V 225A (IVORY) | NAKAJO | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 25.00 min | 6.64 - 6.91 A | 50 | 25 |  |  |  |  | 33058977A | [11 empty] | 1758
| 33058798,D | EX400 3P 250A AC200-440V 100.200.500mA (Ivory) | NAKAJO | 1000200 | 2.81 | 5 | 20 | 26.7 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 12.00 - 16.00 min | 3.43 - 3.57 A | 100 | 25 |  |  |  |  | - | 33059042A | [10 empty] | 1748
| 33058798,C | EX400 3P 300A AC200-440V 100.200.500mA (Ivory) | NAKAJO | 1000200 | 3.38 | 5 | 20 | 26.7 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 13.00 - 19.00 min | 4.17 - 4.34 A | 100 | 25 |  |  |  |  | - | 33059042A | [10 empty] | 1747
| 33058798,B | EX400 3P 350A AC200-440V 100.200.500mA (Ivory) | NAKAJO | 1000200 | 3.94 | 5 | 20 | 26.7 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 12.00 - 16.00 min | 4.90 - 5.10 A | 100 | 25 |  |  |  |  | - | 33059042A | [10 empty] | 1746
| 33058798,A | EX400 3P 400A AC200-440V 100.200.500mA (Ivory) | NAKAJO | 1000200 | 4.5 | 5 | 20 | 26.7 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 13.00 - 18.00 min | 5.48 - 5.70 A | 100 | 25 |  |  |  |  | - | 33059042A | [10 empty] | 1745
| 33047239,B | S-100SB 3P 75A SHT-AUX (DC12V) (New JIS) | NAKAJO | 500100 | 3 | 5 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 5.09 min | 0.98 - 1.02 A | 150 | 25 |  |  |  |  | 33046197B | [11 empty] | 1739
| 33047238,P | S-100EB 2P 75A SHT-AUX (DC12V) (New JIS) | NAKAJO | 500100 | 3 | 5 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 41 sec - 5.09 min | 0.98 - 1.02 A | 150 | 25 |  |  |  |  | 33046169B | [11 empty] | 1738
| 33047239,J | S-125SBY 3P 125A SHT-AUX (DC12V) (New JIS) | NAKAJO | 500100 | 5 | 5 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 1.00 - 6.00 min | 1.62 - 1.69 A | 50 | 25 |  |  |  |  | 33046197M | [11 empty] | 1737
| 33047239,W | S-125SBY 2P 125A SHT-AUX (DC12V) (New JIS) | NAKAJO | 500100 | 5 | 5 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 1.00 - 6.00 min | 1.62 - 1.69 A | 50 | 25 |  |  |  |  | 33046198M | [11 empty] | 1736
| 33058771,T | F-800F 3P 700A (Ivory) | NAKAJO | 1000200 | 3.5 | 5 | 10 | 25 | Lower 200A ∼ 100ms No-Trip | High 500A ∼ 60ms Trip |  | 14.00 - 21.00 min | 7.15 - 7.45 A | 130 | 25 |  |  |  |  | 33058998H | [11 empty] | 1727
| 33058771,S | F-800F 3P 800A (Ivory) | NAKAJO | 1000200 | 4 | 5 | 10 | 25 | Lower 200A ∼ 100ms No-Trip | High 500A ∼ 60ms Trip |  | 14.00 - 18.00 min | 8.18 - 8.51 A | 130 | 25 |  |  |  |  | 33058998H | [11 empty] | 1725
| 33058750,R | FXK60-H 2P 30A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 4.00 - 11.00 min | 1.461 - 1.520 A | 30 | 25 |  |  |  |  | 33058968D | [11 empty] | 1718
| 33058750,B | FXK60-H 3P 50A (IVORY) | NAKAJO | 500100 | 4 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.00 - 11.00 min | 0.494 - 0.514 A | 150 | 25 |  |  |  |  | 33058967B | [11 empty] | 1717
| 33058750,C | FXK60-H 3P 40A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 7.00 - 13.00 min | 0.405 - 0.421 A | 150 | 25 |  |  |  |  | 33058967C | [11 empty] | 1697
| 33058750,E | FXK60-H 3P 20A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.00 - 13.00 min | 0.586 - 0.610 A | 50 | 25 |  |  |  |  | 33058967E | [11 empty] | 1696
| 33059824,J | FXK100-H 3P 100A With AL-1C TB2 | NAKAJO | 500100 | 4 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 8.00 - 13.00 min | 1.047 - 1.090 A | 150 | 25 |  |  |  |  | 33044406B | [11 empty] | 1695
| 33058748,E | FXK60-S 3P 50A ND (IVORY) | NAKAJO | 500100 | 4 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.00 - 11.00 min | 0.494 - 0.514 A | 150 | 25 |  |  |  |  | 33058950B | [11 empty] | 1694
| 33058748,F | FXK60-S 3P 40A ND (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 4.50 - 9.00 min | 1.235 - 1.285 A | 50 | 25 |  |  |  |  | 33058950C | [11 empty] | 1693
| 33058748,G | FXK60-S 3P 30A ND (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 4.00 - 10.00 min | 0.908 - 0.946 A | 50 | 25 |  |  |  |  | 33058950D | [11 empty] | 1692
| 33058748,H | FXK60-S 3P 20A ND (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.00 - 13.00 min | 0.586 - 0.610 A | 50 | 25 |  |  |  |  | 33058950E | [11 empty] | 1691
| 33058748,J | FXK60-S 3P 15A ND (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 7.50 - 13.00 min | 0.449 - 0.467 A | 50 | 25 |  |  |  |  | 33058950F | [11 empty] | 1689
| 33058762,M | S-400S 3P 250A WTMN Naigai Denki (Ivory) | NAKAJO | 1000200 | 3.13 | 5 | 20 | 24 | Lower 1,000% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip |  | 15.00 - 26.00 min | 6.64 -6.91 A | 50 | 25 |  |  |  |  | 33058984A | [11 empty] | 1570
| 33058762,L | S-400S 3P 300A WTMN Naigai Denki (Ivory) | NAKAJO | 1000200 | 3.75 | 5 | 20 | 24 | Lower 1,000% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip |  | 14.00 - 21.00 min | 8.08 - 8.41 A | 50 | 25 |  |  |  |  | 33058984A | [11 empty] | 1557
| 33058762,K | S-400S 3P 350A WTMN Naigai Denki (Ivory) | NAKAJO | 1000200 | 4.16 | 5 | 20 | 23.2 | Lower 950% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip |  | 13.00 - 25.00 min | 8.98 - 9.35 A | 50 | 25 |  |  |  |  | 33058984A | [11 empty] | 1554
| 33058762,J | S-400S 3P 400A WTMN Naigai Denki (Ivory) | NAKAJO | 1000200 | 4.5 | 5 | 20 | 24.4 | Lower 900% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip |  | 14.00 - 28.00 min | 5.10 - 5.31 A | 100 | 25 |  |  |  |  | 33058984A | [11 empty] | 1549
| 33058750,S | FXK60-H 2P 20A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.00 - 22.00 min | 0.940 - 0.978 A | 30 | 25 |  |  |  |  | 33058968E | [11 empty] | 1546
| 33058765,A | S-400S 3P 400A ND (Ivory) | NAKAJO | 1000200 | 4.5 | 5 | 20 | 24.4 | Lower 900% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip |  | 14.00 - 28.00 min | 5.10 - 5.31 A | 100 | 25 |  |  |  |  | 33058984A | [11 empty] | 1545
400AF ND J | 33058765,B | S-400S 3P 350A ND (Ivory) | NAKAJO | 1000200 | 4.16 | 5 | 20 | 23.2 | Lower 950% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip | 120 | 13.00 - 25.00 min | 8.98 - 9.35 A | 50 | 25 | - | - | - | - | 33058984A | - | "58984A" | "JP33058765B" | 1501-4193 | (M10X30) | (M6X45) | - | -
| 33058765,C | S-400S 3P 300A ND (Ivory) | NAKAJO | 1000200 | 3.75 | 5 | 20 | 24 | Lower 1,000% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip |  | 14.00 - 21.00 min | 8.08 - 8.41 A | 50 | 25 |  |  |  |  | 33058984A | [11 empty] | 1543
| 33058765,D | S-400S 3P 250A ND (Ivory) | NAKAJO | 1000200 | 3.13 | 5 | 20 | 24 | Lower 1,000% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip |  | 15.00 - 26.00 min | 6.64 -6.91 A | 50 | 25 |  |  |  |  | 33058984A | [11 empty] | 1540
| 33058767,A | F-400FB 3P 400A (IVORY) | NAKAJO | 1000200 | 4.5 | 5 | 20 | 24.4 | Lower 900% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip |  | 14.00 - 28.00 min | 5.10 - 5.31 A | 100 | 25 |  |  |  |  | 33058984C | [11 empty] | 1513
| 33058767,B | F-400FB 3P 350A (IVORY) | NAKAJO | 1000200 | 4.16 | 5 | 20 | 23.2 | Lower 950% ∼ 100ms No-Trip | High 1,100% ∼ 60ms Trip |  | 13.00 - 25.00 min | 8.98 - 9.35 A | 50 | 25 |  |  |  |  | 33058984C | [11 empty] | 1512
| 33058767,C | F-400FB 3P 300A (IVORY) | NAKAJO | 1000200 | 3.75 | 5 | 20 | 24 | Lower 1,000% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip |  | 14.00 - 21.00 min | 8.08 - 8.41 A | 50 | 25 |  |  |  |  | 33058984C | [11 empty] | 1289
| 33058767,D | F-400FB 3P 250A (IVORY) | NAKAJO | 1000200 | 3.13 | 5 | 20 | 24 | Lower 1,000% ∼ 100ms No-Trip | High 1,200% ∼ 60ms Trip |  | 15.00 - 26.00 min | 6.64 -6.91 A | 50 | 25 |  |  |  |  | 33058984C | [11 empty] | 1288
| 33058750,T | FXK60-H 2P 15A (IVOTY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.00 - 20.00 min | 0.939 - 0.977 A | 30 | 25 |  |  |  |  | 33058968F | [11 empty] | 1287
| 33058827,L | F-225KC 4P 175A (IVORY) | NAKAJO | 1000200 | 2.63 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,550% ∼ 60ms Trip |  | 8.00 - 16.00 min | 5.16 - 5.37 A | 50 | 25 |  |  |  |  | 33058985B | [11 empty] | 1285
| 33058827,N | F-225KC 4P 125A (IVORY) | NAKAJO | 1000200 | 1.88 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,380% ∼ 60ms Trip |  | 6.00 - 14.00 min | 3.65 - 3.80 A | 50 | 25 |  |  |  |  | 33058985B | [11 empty] | 1277
| 33058754,E | FXK50-HU 2P 10A (IVORY) | NAKAJO | 100(X20) | 4 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 2.00 min | 1.31 - 1.36 A | 15 | 25 |  |  |  |  | 33058970A | [11 empty] | 1237
| 33058754,F | FXK50-HU 2P 5A (IVORY) | NAKAJO | 100(X20) | 2 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 2.00 min | 0.65 - 0.68 A | 15 | 25 |  |  |  |  | 33058970B | [11 empty] | 1236
| 33058754,B | FXK50-HU 3P 5A (IVORY) | NAKAJO | 100(X20) | 2 | 10 | 10 | 25 | Lower 800A ∼ 60ms No-Trip | High 2,000A ∼ 100ms Trip |  | 40 sec - 2.00 min | 0.65 - 0.68 A | 15 | 25 |  |  |  |  | 33058969B | [11 empty] | 1226
| 33058793,A | EXK225 3P 225A 30mA (Ivory) | NAKAJO | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 8.00 - 17.00 min | 6.64 -6.91 A | 50 | 25 |  |  |  |  | - | 33059022A | [10 empty] | 1224
| 33058793,B | EXK225 3P 200A 30mA (Ivory) | NAKAJO | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 10.00 min | 6.64 -6.91 A | 50 | 25 |  |  |  |  | - | 33059022A | [10 empty] | 966
| 33058793,E | EXK225 3P 125A 30mA (Ivory) | NAKAJO | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 6.00 - 15.00 min | 4.25 - 4.42 A | 50 | 25 |  |  |  |  | - | 33059022A | [10 empty] | 965
| 33058771,B | S-600S 3P 500A (Ivory) | NAKAJO | 1000200 | 2.5 | 5 | 10 | 25 | Lower 200A ∼ 100ms No-Trip | High 500A ∼ 60ms Trip |  | 14.00 - 18.00 min | 7.40 - 7.70 A | 90 | 25 |  |  |  |  | 33058998A | [11 empty] | 747
| 33058771,A | S-600S 3P 600A (Ivory) | NAKAJO | 1000200 | 3 | 5 | 10 | 25 | Lower 200A ∼ 100ms No-Trip | High 500A ∼ 60ms Trip |  | 20.00 - 27.00 min | 8.27 - 8.61 A | 90 | 25 |  |  |  |  | 33058998A | [11 empty] | 746
| 33058771,F | F-600F 3P 500A (Ivory) | NAKAJO | 1000200 | 2.5 | 5 | 10 | 25 | Lower 200A ∼ 100ms No-Trip | High 500A ∼ 60ms Trip |  | 14.00 - 18.00 min | 7.40 - 7.70 A | 90 | 25 |  |  |  |  | 33058998E | [11 empty] | 745
| 33058771,E | F-600F 3P 600A (Ivory) | NAKAJO | 1000200 | 3 | 5 | 10 | 25 | Lower 200A ∼ 100ms No-Trip | High 500A ∼ 60ms Trip |  | 20.00 - 27.00 min | 8.27 - 8.61 A | 90 | 25 |  |  |  |  | 33058998E | [11 empty] | 744
| 33058787,B | RXK125-SA 3P 100A AC100-440V 30mA (Ivory) | NAKAJO | 500100 | 4 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.00 - 9.30 min | 1.012 - 1.053 A | 150 | 25 |  |  |  |  | 33058954B | 33058960A | [10 empty] | 740
| 33058787,C | RXK125-SA 3P 75A AC100-440V 30mA (Ivory) | NAKAJO | 500100 | 3 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.30 - 13.30 min | 0.745 - 0.776 A | 150 | 25 |  |  |  |  | 33058954C | 33058960A | [10 empty] | 738
| 33058787,D | RXK125-SA 3P 60A AC100-440V 30mA (Ivory) | NAKAJO | 500100 | 4.8 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.00 - 10.00 min | 0.623 - 0.649 A | 150 | 25 |  |  |  |  | 33058954D | 33058960A | [10 empty] | 731
| 33058787,E | RXK125-SA 3P 50A AC100-440V 30mA (Ivory) | NAKAJO | 500100 | 4 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.00 - 12.00 min | 0.516 - 0.537 A | 150 | 25 |  |  |  |  | 33058954E | 33058960A | [10 empty] | 729
| 33058787,F | RXK125-SA 3P 40A AC100-440V 30mA (Ivory) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 4.30 - 10.00 min | 1.218 - 1.268 A | 50 | 25 |  |  |  |  | 33058954F | 33058960A | [10 empty] | 726
| 33058787,G | RXK125-SA 3P 30A AC100-440V 30mA (Ivory) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.30 - 12.00 min | 0.919 - 0.957 A | 50 | 25 |  |  |  |  | 33058954G | 33058960A | [10 empty] | 724
| 33058787,H | RXK125-SA 3P 20A AC100-440V 30mA (Ivory) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 7.00- 14.30 min | 0.587 - 0.611 A | 50 | 25 |  |  |  |  | 33058954H | 33058960A | [10 empty] | 722
| 33058787,J | RXK125-SA 3P 15A AC100-440V 30mA (Ivory) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 7.30 - 13.00 min | 0.453 - 0.471 A | 50 | 25 |  |  |  |  | 33058954J | 33058960A | [10 empty] | 721
| 33058750,F | FXK60-H 3P 15A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.00 - 11.00 min | 0.694 - 0.723 A | 30 | 25 |  |  |  |  | 33058967F | [11 empty] | 718
| 33058787,P | RXK125-SA 3P 100A AC100-440V 100.200.500mA (Ivory) | NAKAJO | 500100 | 4 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.00 - 9.30 min | 1.012 - 1.053 A | 150 | 25 |  |  |  |  | 33058954L | 33058961A | [10 empty] | 716
| 33058787,Q | RXK125-SA 3P 75A AC100-440V 100.200.500mA (Ivory) | NAKAJO | 500100 | 3 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.30 - 13.30 min | 0.745 - 0.776 A | 150 | 25 |  |  |  |  | 33058954M | 33058961A | [10 empty] | 714
| 33058787,R | RXK125-SA 3P 60A AC100-440V 100.200.500mA (Ivory) | NAKAJO | 500100 | 4.8 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.00 - 10.00 min | 0.623 - 0.649 A | 150 | 25 |  |  |  |  | 33058954N | 33058961A | [10 empty] | 713
| 33058787,S | RXK125-SA 3P 50A AC100-440V 100.200.500mA (Ivory) | NAKAJO | 500100 | 4 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.00 - 12.00 min | 0.516 - 0.537 A | 150 | 25 |  |  |  |  | 33058954P | 33058961A | [10 empty] | 712
| 33058787,T | RXK125-SA 3P 40A AC100-440V 100.200.500mA (Ivory) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 4.30 - 10.00 min | 1.218 - 1.268 A | 50 | 25 |  |  |  |  | 33058954Q | 33058961A | [10 empty] | 711
| 33058787,U | RXK125-SA 3P 30A AC100-440V 100.200.500mA (Ivory) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.30 - 12.00 min | 0.919 - 0.957 A | 50 | 25 |  |  |  |  | 33058954R | 33058961A | [10 empty] | 710
| 33058787,V | RXK125-SA 3P 20A AC100-440V 100.200.500mA (Ivory) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 7.00- 14.30 min | 0.587 - 0.611 A | 50 | 25 |  |  |  |  | 33058954S | 33058961A | [10 empty] | 709
| 33058787,W | RXK125-SA 3P 15A AC100-440V 100.200.500mA (Ivory) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 7.30 - 13.00 min | 0.453 - 0.471 A | 50 | 25 |  |  |  |  | 33058954T | 33058961A | [10 empty] | 708
| 33058745,E | SXK125-C 3P 50A (IVORY) | NAKAJO | 500100 | 4 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 5.00 - 11.00 min | 0.494 - 0.514 A | 150 | 25 |  |  |  |  | 33058949E | [11 empty] | 705
| 33058745,A | SXK125-C 3P 125A (IVORY) | NAKAJO | 500100 | 5 | 5 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 4.50 - 11.00 min | 1.237 - 1.287 A | 150 | 25 |  |  |  |  | 33058949A | [11 empty] | 704
| 33058751,S | FXK125-S 2P 50A (IVORY) | NAKAJO | 500100 | 4 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.00 - 9.00 min | 0.516 - 0.537 A | 150 | 25 |  |  |  |  | 33058966R | [11 empty] | 703
| 33047246,M | EX225 3P 150A 100.200.500 Ma High speed type AL-AUX-1C TB2 | NAKAJO | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 6.00 - 12.00 min | 4.92 - 5.12 A | 50 | 25 | [5 empty] | 33042990A | [10 empty] | 702
| 33058752,J | FXK125-H 3P 15A (IVORY) | NAKAJO | 500100 | 3.2 | 10 | 15 | 22.5 | Lower 480A ∼ 100ms No-Trip | High 720A ∼ 60ms Trip |  | 5.00 - 14.00 min | 0.694 - 0.723 A | 30 | 25 |  |  |  |  | 33058965J | [11 empty] | 701
| 33058750,A | FXK60-H 3P 60A (IVORY) | NAKAJO | 500100 | 4.8 | 10 | 15 | 22.5 | Lower 1,200% ∼ 100ms No-Trip | High 1,800% ∼ 60ms Trip |  | 6.30 - 13.030 min | 0.626 - 0.652 A | 150 | 25 |  |  |  |  | 33058967A | [11 empty] | 700
| 33058793,J | EXK225 3P 225A 100.200.500mA (Ivory) | NAKAJO | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 8.00 - 17.00 min | 6.64 - 6.91 A | 50 | 25 | [5 empty] | 33059024A | [10 empty] | 694
| 33058793,K | EXK225 3P 200A 100.200.500mA (Ivory) | NAKAJO | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 10.00 min | 6.64 - 6.91 A | 50 | 25 | [5 empty] | 33059024A | [10 empty] | 693
| 33058793,N | EXK225 3P 125A 100.200.500mA (Ivory) | NAKAJO | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 6.00 - 15.00 min | 4.25 - 4.42 A | 50 | 25 | [5 empty] | 33059024A | [10 empty] | 692
| 33058771,N | S-800S 3P 800A (IVORY) | NAKAJO | 1000200 | 4 | 5 | 10 | 25 | Lower 200A ∼ 100ms No-Trip | High 500A ∼ 60ms Trip |  | 14.00 - 18.00 min | 8.18 - 8.51 A | 130 | 25 |  |  |  |  | 33058998C | [11 empty] | 691
| 33058776,K | SX800 3P 800A Y (Ivory) | NAKAJO | - | - | - | - | - | - | - | - | 19 - 30 sec | 1440 - 1760 A | - | - | - | - | - | - | 33058996C | [11 empty] | 690
| 33058776,E | FX600 3P 600A (Ivory) | NAKAJO | - | - | - | - | - | - | - | - | 19 - 30 sec | 1,080 - 1,320 A | - | - | - | - | - | - | 33058996E | [11 empty] | 689
| 33058776,B | SX600 3P 600A Y (Ivory) | NAKAJO | - | - | - | - | - | - | - | - | 19 - 30 sec | 1,080 - 1,320 A | - | - | - | - | - | - | 33058996A | [11 empty] | 688
| 33058776,A | SX600 3P 600A (Ivory) | NAKAJO | - | - | - | - | - | - | - | - | 19 - 30 sec | 1,080 - 1,320 A | - | - | - | - | - | - | 33058996A | [11 empty] | 687
| 33058800,J | EX400B 3P 400A AC200-440V 100.200.500mA (Ivory) | NAKAJO | - | - | - | - | - | - | - | - | 19 - 30 sec | 720 - 880 A | - | - | - | - | - | - | 33059191A | [11 empty] | 686
| 33058759,P | FXK250-H 2P 125A (IVORY) | NAKAJO | 1000200 | 1.88 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 10.40 - 17.00 min | 3.89 - 4.05 A | 50 | 25 |  |  |  |  | 33058978B | [11 empty] | 685
| 33058759,N | FXK250-H 2P 150A (IVORY) | NAKAJO | 1000200 | 2.25 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 9.50 - 16.10 min | 4.59 - 4.78 A | 50 | 25 |  |  |  |  | 33058978B | [11 empty] | 684
| 33058759,M | FXK250-H 2P 175A (IVORY) | NAKAJO | 1000200 | 2.63 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 8.20 - 15.20 min | 5.18 - 5.39 A | 50 | 25 |  |  |  |  | 33058978B | [11 empty] | 683
| 33058759,L | FXK250-H 2P 200A (IVORY) | NAKAJO | 1000200 | 3 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 7.90 - 12.10 min | 6.03 - 6.28 A | 50 | 25 |  |  |  |  | 33058978B | [11 empty] | 682
| 33058759,K | FXK250-H 2P 225A (IVORY) | NAKAJO | 1000200 | 3.38 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 6.00 - 9.50 min | 6.97 - 7.25 A | 50 | 25 |  |  |  |  | 33058978B | [11 empty] | 681
| 33058759,J | FXK250-H 2P 250A (IVORY) | NAKAJO | 1000200 | 3.75 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 7.10 - 9.50 min | 3.78 - 3.94 A | 100 | 25 |  |  |  |  | 33058978B | [11 empty] | 680
| 33058756,N | SXK225 2P 125A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 25.00 min | 4.25 - 4.42 A | 50 | 25 |  |  |  |  | 33058974B | [11 empty] | 679
| 33058756,M | SXK225 2P 150A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 25.00 min | 4.92 - 5.12 A | 50 | 25 |  |  |  |  | 33058974B | [11 empty] | 678
| 33058756,L | SXK225 2P 175A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 2.41 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 25.00 min | 5.80 - 6.04 A | 50 | 25 |  |  |  |  | 33058974B | [11 empty] | 677
| 33058756,K | SXK225 2P 200A (IVORY) (5PCS/BOX) | NAKAJO | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 20.00 min | 6.64 - 6.91 A | 50 | 25 |  |  |  |  | 33058974B | [11 empty] | 676
| 33058756,J | SXK225 2P 225A (IVORY) (5PCS/BOX) | NAKAJO | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.00 - 25.00 min | 6.64 - 6.91 A | 50 | 25 |  |  |  |  | 33058974B | [11 empty] | 675
| 33058756,E | SXK225 3P 125A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 8.00 - 9.30 min | 3.85 - 4.01 A | 50 | 25 |  |  |  |  | 33058974A | [11 empty] | 674
| 33058756,D | SXK225 3P 150A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.30 - 10.00 min | 4.44 - 4.62 A | 50 | 25 |  |  |  |  | 33058974A | [11 empty] | 673
| 33058756,C | SXK225 3P 175A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 2.41 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 8.00 - 16.30 min | 5.24 - 5.45 A | 50 | 25 |  |  |  |  | 33058974A | [11 empty] | 672
| 33058756,B | SXK225 3P 200A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 6.00 - 10.00 min | 6.00 - 6.24 A | 50 | 25 |  |  |  |  | 33058974A | [11 empty] | 671
| 33058756,A | SXK225 3P 225A (Ivory) (5PCS/BOX) | NAKAJO | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 8.30 - 21.00 min | 5.93 - 6.17 A | 50 | 25 |  |  |  |  | 33058974A | [11 empty] | 670
| 33058757,D | SXK225 3P 150A (IVORY) ND | NAKAJO | 1000200 | 2.06 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 5.30 - 10.00 min | 4.44 - 4.62 A | 50 | 25 |  |  |  |  | 33058974A | [11 empty] | 669
| 33058757,E | SXK225 3P 125A (IVORY) ND | NAKAJO | 1000200 | 1.72 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 8.00 - 9.30 min | 3.85 - 4.01 A | 50 | 25 |  |  |  |  | 33058974A | [11 empty] | 668
| 33058757,B | SXK225 3P 200A (IVORY) ND | NAKAJO | 1000200 | 2.75 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 6.00 - 10.00 min | 6.00 - 6.24 A | 50 | 25 |  |  |  |  | 33058974A | [11 empty] | 667
| 33058757,C | SXK225 3P 175A (IVORY) ND | NAKAJO | 1000200 | 2.41 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 8.00 - 16.30 min | 5.24 - 5.45 a | 50 | 25 |  |  |  |  | 33058974A | [11 empty] | 666
| 33058757,A | SXK225 3P 225A (IVORY) ND | NAKAJO | 1000200 | 3.09 | 5 | 20 | 23.6 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 8.30 - 21.00 min | 5.93 - 6.17 A | 50 | 25 |  |  |  |  | 33058974A | [11 empty] | 665
| 33058758,K | FXK250-S 2P 225A (IVORY) | NAKAJO | 1000200 | 3.38 | 5 | 20 | 26.7 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 6.00 - 9.50 min | 6.97 - 7.25 A | 50 | 25 |  |  |  |  | 33058978D | [11 empty] | 664
| 33058758,J | FXK250-S 2P 250A (IVORY) | NAKAJO | 1000200 | 3.75 | 5 | 20 | 26.7 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 7.10 - 9.50 min | 3.78 - 3.94 A | 100 | 25 |  |  |  |  | 33058978D | [11 empty] | 663
| 33058758,N | FXK250-S 2P 150A (IVORY) | NAKAJO | 1000200 | 2.25 | 5 | 20 | 26.7 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 9.50 - 16.1 min | 4.59 - 4.78 A | 50 | 25 |  |  |  |  | 33058978D | [11 empty] | 662
| 33058758,P | FXK250-S 2P 125A (IVORY) | NAKAJO | 1000200 | 1.88 | 5 | 20 | 26.7 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 10.40 - 17.00 min | 3.89 - 4.05 A | 50 | 25 |  |  |  |  | 33058978D | [11 empty] | 661
| 33058758,A | FXK250-S 3P 250A (Ivory) ND | NAKAJO | 1000200 | 3.75 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 7.10 - 9.50 min | 3.78 - 3.94 A | 100 | 25 |  |  |  |  | 33058978C | [11 empty] | 660
| 33058758,F | FXK250-S 3P 125A (IVORY) | NAKAJO | 1000200 | 1.88 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 10.40 - 17.00 min | 3.89 - 4.05 A | 50 | 25 |  |  |  |  | 33058978C | [11 empty] | 659
| 33058759,A | FXK250-H 3P 250A (IVORY) | NAKAJO | 1000200 | 3.75 | 5 | 20 | 26.7 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 7.10 - 9.50 min | 3.78 - 3.94 A | 100 | 25 |  |  |  |  | 33058978A | [11 empty] | 658
| 33058759,B | FXK250-H 3P 225A (IVORY) | NAKAJO | 1000200 | 3.38 | 5 | 20 | 26.7 | Lower 1,200% ∼ 100ms No-Trip | High 1,600% ∼ 60ms Trip |  | 6.00 - 9.50 min | 6.97 - 7.25 A | 50 | 25 |  |  |  |  | 33058978A | [11 empty] | 657
| 33058759,D | FXK250-H 3P 175A (IVORY) | NAKAJO | 1000200 | 2.63 | 5 | 20 | 26.7 | Lower 1,100% ∼ 100ms No-Trip | High 1,300% ∼ 60ms Trip |  | 8.20 - 15.20 min | 5.18 - 5.39 A | 50 | 25 |  |  |  |  | 33058978A | [11 empty] | 656

## Sheet2
Results
F/G | 33058755,A | **ใส่ค่าเหมือน colum B ของ sheet "DATA"
Form | #N/A | **ได้ค่ากลับมาเป็น colum A ของ sheet "DATA"