## Record
ANALYSIS RESULT OF WASTE WATER TREATMENT
[9 empty] | Approve | Analysis
Discharge tank No. | 1 |  |  | SAMPLING DATE: | 2019-04-01 | TIME : | 14.2
[5 empty] | Start |  | Finish
Report No. | REC-2019-001 |  |  | ANALYSIS DATE: | 2019-04-01 |  | 2019-04-03
Sample | pH Value | Temp. | %RPD, | Color |  |  |  | %RPD,
| (± 0.05) | (± 0.1) | %Recovery | pH Vlue | Original Sample Result (ADMI) | pH Vlue | pH adjusted at 7.00 Result (ADMI) | %Recovery
|  |  | (90-110%) |  |  |  |  | (70-110%)
LCS (pH 7.00) *
LCS (platnum-coblt) 100( ADMI) |  |  |  | - | 102 | - | - | 102
Discharge 1 | 7.54 | 22.9 | - | 7.54 | 17 | 7.03 | 34
Duplicate ** |  |  |  | 7.54 | 20 | 7.02 | 34
%RPD | - | - | -
Sample | Heavy Metal (mg/L)
| Dilution | Cu Result | %RPD, | Zn Result | %RPD, | Cr Result | %RPD, | Ni Result | %RPD,
|  |  | %Recovery ! |  | %Recovery ! |  | %Recovery ! |  | %Recovery !
LCS (STD 1.00 mg/L) ! | 1 | 1.03 | 103 | 1.07 | 107 | 102 | 102 | 0.99 | 99
Discharge 1 | 1 | ND | - | 0.01 | - | ND | - | ND | -
Duplicate ** | 1 | ND | 0 | 0.01 | 0 | ND | 0 | ND | 0
Matrix Spike ***+!
Sample | Sample | Volume of FAS |  |  | COD = (A-B) X M X 8000 X %Sample Dilution /ml. Sample |  |  |  | Result (mg/L) | %RPD,
| (ml) | After (ml) | Before (ml) | A-B (ml) | (A-B)bl- (A-B)Sam. | Factor of FAS | Dilution | Result (mg/L) |  | %Recovery !!
Method Blank | 2.5 |  |  | 0 | - |  | - |  | ND | -
Method Blank (Dilution case) |  |  |  | 0 | - |  | - |  | - | -
LCS (KHP 200 mg/L)*+!! | 2.5 |  |  | 0 | 0 |  |  |  | 214.16 | 107.08
Discharge 1 | 2.5 |  |  | 0 | 0 |  |  |  | 258.12 | -
Duplicate ** | 2.5 |  |  | 0 | 0 |  |  |  | 255.77 | 0.91459
Spike (KHP 200mg/L) ***+!! | 2.5 |  |  | 0 | 0 |  |  |  | 412.26 | 77.07
Duplicate Spike ** | 2.5 |  |  | 0 | 0 |  |  |  | 420.76 | 2.0408
Sample |  | Total Dissolved Solid | [6 empty] | Result (mg/L) | %RPD,
| Sample | After (A) |  |  | Before (B) |  |  | A-B |  | %Recovery
| (ml) | Weight 1 | Weight 2 | Average | Weight 1 | Weight 2 | Average |  |  | (90-110%)
Discharge 1 | 25 | 96.7169 | 96.7171 | 96.717 | 96.6718 | 96.6714 | 96.6716 | 0.0454 | 1816 | -
Duplicate ** | 25 | 117.8279 | 117.8282 | 117.828 | 117.7821 | 117.7826 | 117.7824 | 0.0457 | 1828 | 0.65862
Sample |  | Suspended Solid | [6 empty] | Result (mg/L) | %RPD,
| Sample | After (A) |  |  | Before (B) |  |  | A-B |  | %Recovery
| (ml) | Weight 1 | Weight 2 | Average | Weight 1 | Weight 2 | Average |  |  | (90-110%)
Method Blank | 150 | 2.2507 | 2.2504 | 2.2506 | 2.2502 | 2.2507 | 2.2504 | 0.0001 | 0.66667 | -
LCS (Cellulose 50 mg/L) * | 500 | 2.2626 | 2.2631 | 2.2629 | 2.239 | 2.239 | 2.239 | 0.02385 | 47.7 | 95.4
Discharge 1 | 115 | 2.2328 | 2.2327 | 2.2328 | 2.2266 | 2.2268 | 2.2267 | 0.00605 | 52.6087 | -
Duplicate ** | 115 | 2.2296 | 2.2294 | 2.2295 | 2.2229 | 2.2229 | 2.2229 | 0.0066 | 57.3913 | 8.6957
Sample |  | Oil & Grease | [6 empty] | Result (mg/L) | %RPD,
| Sample | After (A) |  |  | Before (B) |  |  | A-B |  | %Recovery
| (ml) | Weight 1 | Weight 2 | Average | Weight 1 | Weight 2 | Average |  |  | (70-110%)
Method Blank | 1000 | 71.5108 | 71.5111 | 71.511 | 71.5116 | 71.5111 | 71.5113 | -0.0004 | -0.4 | -
Spike (STD.Oil 40 mg/L) * | 1000 | 75.0385 | 75.0385 | 75.0385 | 75.0143 | 75.0146 | 75.0145 | 0.02405 | 24.05 | 60.125
Duplicate Spike ** | 1000 | 70.8725 | 70.872 | 70.8723 | 70.848 | 70.848 | 70.848 | 0.02425 | 24.25 | 0.82816
Discharge 1 | 1100 | 71.6996 | 71.6901 | 71.6949 | 71.6897 | 71.6899 | 71.6898 | 0.00505 | 4.5909 | -
Calculation : | *1) LCS(Lab Control Sample)
; X2 = Concentration of Check , X1 = Concentration of Preparation
| **2) Duplicate |  |  |  | (STD.%RPD ≤ 10)
; X1 = Result of Check No.1, X2 = Result of Check No. 2 , = Average of Result
***3) Matrix Spike
; Xs = Concentration of Spike Sample , Xu = Concentration of Sample , K = Concentration of Solution
! 4) %Recovery 85-115
!! 5) %Recovery 90-110
%RPD=(X_1 〖−X〗_2×100)/¯X
¯X
%Recovery=(X_2×100)/X_1
Add New Record
Save Record
%Recovery="100" (〖"X" _"s" "−X" 〗_"u" )/"K"
Note on A10: 1006968: % Recovery 90-110
Note on A13: 1006968: Duplicate = > % RPD 10% MAX
Note on A14: 1006968: Spike STD. ลงในน้ำตัวอย่าง % Recovery 85-115 For heavy metal
Note on A19: 1006968: % Recovery 85-115
Note on A21: 1006968: Duplicate = > % RPD 10% MAX
Note on N21: 1006968: Duplicate = > % RPD 10% MAX
Note on A22: 1006968: Spike STD. ลงในน้ำตัวอย่าง % Recovery 85-115 For heavy metal
Note on H25: 1006968: ใส่ จำนวนเท่าที่ dil. ไม่ได้ dilute ใส่ 1 10/50 คูณ oil batch 1/250 คูณ250เท่า
Note on G27: 1006968: factor กรณ๊ dil. **** เปลี่ยนสูตร ให้ถูกต้องด้วย ใน (A-B)BL - (A-B)SAMPLE
Note on A28: 1006968: % Recovery 90-110
Note on A30: 1006968: Duplicate = > % RPD 10% MAX
Note on K30: 1006968: Dul. Sample ใด แก้สูตรด้วย
Note on A31: 1006968: %Recovery 90-110%
Note on K31: 1006968: Spike ลงตัวอย่างใด แก้สูตรด้วย
Note on A32: 1006968: Duplicate = > % RPD 10% MAX
Note on K32: 1006968: ไม่ต้องแก้สูตร เพราะ Dup spike อยู่แร้ว
Note on A38: 1006968: Duplicate = > % RPD 10% MAX
Note on K38: 1006968: Dul. Sample ใด แก้สูตรด้วย
Note on A44: 1006968: % Recovery 90-110
Note on A46: 1006968: Duplicate = > % RPD 10% MAX
Note on K46: 1006968: Dul. Sample ใด แก้สูตรด้วย
Note on A52: 1006968: % Recovery 70-110
Note on A53: 1006968: Duplicate = > % RPD 10% MAX
Note on K53: 1006968: ไม่ต้องแก้สูตร Dup. spike อยู่แล้ว

## Discharge
|  |  | Parameter | Oil & Grease |  | <<เลือก Parameter ที่ต้องการดู
|  |  | > เลือกช่วงเวลาที่ต้องการติดตามโดยใช้ Filter | [12 empty] | Upper limit |  | Lower limit |  | Parameter
Report No. | Year | Month | Date | Discharge No. | pH | Oil & Grease | COD | TSS | TDS | Cu | Zn | Cr | Ni | Color | BOD | IEAT STD. | DECO STD | IEAT STD.2 | DECO STD3 | Actual
2019-001 | 2019 | เม.ย. | 2019-04-01 | 2 | 7.54 | 4.6 | 258 | 53 | 1816 | 0 | 0.01 | 0 | 0 |  |  | 10 | 7.5 |  |  | 4.6
2019-002 | 2019 | เม.ย. | 2019-04-03 | 3 | 7.31 | 3.1 | 274 | 65 | 1652 | 0.03 | 0.95 | 0 | 0 |  |  | 10 | 7.5 |  |  | 3.1
2019-003 | 2019 | เม.ย. | 2019-04-08 | 2 | 7.17 | 4.3 | 172 | 55 | 1540 | 0 | 0.17 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 4.3
2019-004 | 2019 | เม.ย. | 2019-04-09 | 3 | 7.28 | 9.3 | 195 | 68 | 1678 | 0.01 | 0.66 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 9.3
2019-005 | 2019 | เม.ย. | 2019-04-18 | 1 | 6.91 | 1.5 | 207 | 24 | 1696 | 0.01 | 1.09 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 1.5
2019-006 | 2019 | เม.ย. | 2019-04-18 | 3 | 6.89 | 3 | 109 | 23 | 1392 | 0.01 | 0.51 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 3
2019-007 | 2019 | เม.ย. | 2019-04-19 | 2 | 7.09 | 3.7 | 80 | 13 | 1334 | 0.01 | 1.3 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 3.7
2019-008 | 2019 | เม.ย. | 2019-04-26 | 1 | 7.12 | 1.7 | 248 | 25 | 1386 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.7
2019-009 | 2019 | เม.ย. | 2019-04-26 | 2 | 7.23 | 3.5 | 153 | 33 | 1100 | 0.01 | 0.01 | 0 | 0 |  |  | 10 | 7.5 |  |  | 3.5
2019-010 | 2019 | เม.ย. | 2019-04-29 | 3 | 7.6 | 1.4 | 74 | 12 | 758 | 0 | 0.2 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.4
2019-011 | 2019 | เม.ย. | 2019-04-30 | 2 | 7.85 | 3.2 | 279 | 20 | 1102 | 0 | 0.65 | 0 | 0 |  |  | 10 | 7.5 |  |  | 3.2
2019-012 | 2019 | พ.ค. | 2019-05-07 | 1 | 7.65 | 0 | 305 | 9 | 1332 | 0.02 | 0.88 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2019-013 | 2019 | พ.ค. | 2019-05-08 | 2 | 7.87 | 0 | 261 | 11 | 1302 | 0.02 | 0.56 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0
2019-014 | 2019 | พ.ค. | 2019-05-13 | 3 | 7.9 | 0 | 338 | 10 | 1408 | 0.05 | 0.12 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2019-015 | 2019 | พ.ค. | 2019-05-15 | 1 | 7.99 | 6.1 | 427 | 28 | 1258 | 0.07 | 0.63 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 6.1
2019-016 | 2019 | พ.ค. | 2019-05-17 | 3 | 7.8 | 2.5 | 175 | 35 | 1108 | 0 | 0.22 | 0 | 0 |  |  | 10 | 7.5 |  |  | 2.5
2019-017 | 2019 | พ.ค. | 2019-05-23 | 3 | 8.04 | 0.7 | 132 | 17 | 1120 | 0 | 0.78 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.7
2019-018 | 2019 | พ.ค. | 2019-05-25 | 2 | 7.87 | 0.8 | 150 | 46 | 992 | 0.01 | 0.9 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0.8
2019-019 | 2019 | พ.ค. | 2019-05-27 | 3 | 7.92 | 2.8 | 124 | 31 | 1108 | 0.05 | 0.31 | 0 | 0 |  |  | 10 | 7.5 |  |  | 2.8
2019-020 | 2019 | พ.ค. | 2019-05-29 | 2 | 7 | 0.8 | 99 | 20 | 914 | 0.04 | 0.83 | 0.01 | 0 |  |  | 10 | 7.5 |  |  | 0.8
2019-021 | 2019 | มิ.ย. | 2019-06-04 | 2 | 7.75 | 3.4 | 330 | 41 | 1650 | 0.04 | 0.04 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 3.4
2019-022 | 2019 | มิ.ย. | 2019-06-04 | 3 | 7.89 | 4.3 | 186 | 44 | 1778 | 0.04 | 0.02 | 0 | 0 |  |  | 10 | 7.5 |  |  | 4.3
2019-023 | 2019 | มิ.ย. | 2019-06-12 | 2 | 7.58 | 0 | 414 | 18 | 1684 | 0 | 0.72 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2019-024 | 2019 | มิ.ย. | 2019-06-14 | 1 | 7.9 | 4.6 | 490 | 16 | 1404 | 0.06 | 0.22 | 0 | 0 |  |  | 10 | 7.5 |  |  | 4.6
2019-025 | 2019 | มิ.ย. | 2019-06-20 | 3 | 7.54 | 2.4 | 518 | 13 | 1766 | 0.05 | 0.01 | 0 | 0 |  |  | 10 | 7.5 |  |  | 2.4
2019-026 | 2019 | มิ.ย. | 2019-06-22 | 1 | 7.45 | 4.1 | 438 | 6 | 412 | 0.03 | 0 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 4.1
2019-027 | 2019 | มิ.ย. | 2019-06-26 | 3 | 7.86 | 1.7 | 218 | 13 | 1378 | 0.05 | 0.39 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 1.7
2019-028 | 2019 | ก.ค. | 2019-07-02 | 2 | 7.39 | 0.4 | 335 | 8 | 1614 | 0.04 | 0.39 | 0 | 0.05 |  |  | 10 | 7.5 |  |  | 0.4
2019-029 | 2019 | ก.ค. | 2019-07-08 | 3 | 7.53 | 1.9 | 236 | 25 | 1712 | 0.05 | 0.12 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 1.9
2019-030 | 2019 | ก.ค. | 2019-07-20 | 1 | 8.06 | 3.2 | 133 | 30 | 1522 | 0.02 | 0.21 | 0 | 0 |  |  | 10 | 7.5 |  |  | 3.2
2019-031 | 2019 | ก.ค. | 2019-07-24 | 2 | 7.98 | 1.5 | 181 | 62 | 1588 | 0.05 | 0.2 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 1.5
2019-032 | 2019 | ก.ค. | 2019-07-26 | 3 | 8.14 | 2 | 145 | 142 | 102 | 0.05 | 0.3 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 2
2019-033 | 2019 | ส.ค. | 2019-08-02 | 2 | 8.28 | 2.7 | 221 | 69 | 1594 | 0 | 0.51 | 0 | 0.05 |  |  | 10 | 7.5 |  |  | 2.7
2019-034 | 2019 | ส.ค. | 2019-08-06 | 2 | 8.05 | 1.6 | 228 | 48 | 1644 | 0.04 | 0.55 | 0 | 0.05 |  |  | 10 | 7.5 |  |  | 1.6
2019-035 | 2019 | ส.ค. | 2019-08-06 | 3 | 8.06 | 3.2 | 204 | 40 | 1608 | 0.03 | 0.88 | 0 | 0.05 |  |  | 10 | 7.5 |  |  | 3.2
2019-036 | 2019 | ส.ค. | 2019-08-14 | 2 | 8.1 | 2.5 | 189 | 49 | 1896 | 0.45 | 0.07 | 0 | 0 |  |  | 10 | 7.5 |  |  | 2.5
2019-037 | 2019 | ส.ค. | 2019-08-14 | 3 | 7.91 | 1.6 | 229 | 34 | 1816 | 0.14 | 0.03 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.6
2019-038 | 2019 | ส.ค. | 2019-08-20 | 2 | 7.93 | 1.2 | 127 | 45 | 1380 | 0.07 | 0.19 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 1.2
2019-039 | 2019 | ส.ค. | 2019-08-20 | 3 | 8.03 | 0.8 | 126 | 20 | 1034 | 0.04 | 0.15 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0.8
2019-040 | 2019 | ส.ค. | 2019-08-26 | 2 | 7.84 | 0 | 704 | 32 | 1776 | 0.01 | 0.26 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2019-041 | 2019 | ส.ค. | 2019-08-29 | 3 | 8.02 | 1.1 | 802 | 160 | 2726 | 0 | 0.66 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.1
2019-042 | 2019 | ส.ค. | 2019-08-30 | 2 | 8.27 | 1.8 | 635 | 21 | 3104 | 0 | 0.6 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.8
2019-043 | 2019 | ส.ค. | 2019-08-31 | 2 | 7.62 | 1.5 | 179 | 9 | 1196 | 0 | 0.36 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.5
2019-044 | 2019 | ส.ค. | 2019-08-31 | 3 | 7.34 | 1.4 | 189 | 10 | 848 | 0 | 0.41 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.4
2019-045 | 2019 | ก.ย. | 2019-09-04 | 1 | 8.26 | 0.69 | 422.54 | 53 | 2430 | 0 | 0.43 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.69
2019-046 | 2019 | ก.ย. | 2019-09-06 | 1 | 8.11 | 0.14 | 190.7 | 33 | 1390 | 0 | 0.68 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0.14
2019-047 | 2019 | ก.ย. | 2019-09-10 | 1 | 8.16 | 1.44 | 239.57 | 50 | 1470 | 0.03 | 1.14 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 1.44
2019-048 | 2019 | ก.ย. | 2019-09-14 | 1 | 7.42 | 2.76 | 70.64 | 7 | 864 | 0 | 0.39 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 2.76
2019-049 | 2019 | ก.ย. | 2019-09-14 | 3 | 7.55 | 2.93 | 81.87 | 20 | 1298 | 0 | 0.42 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 2.93
2019-050 | 2019 | ก.ย. | 2019-09-17 | 2 | 7.88 | 0 | 231.11 | 13 | 1602 | 0 | 0.52 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0
2019-051 | 2019 | ก.ย. | 2019-09-18 | 3 | 7.97 | 1.15 | 373.21 | 35 | 2028 | 0 | 0.3 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 1.15
2019-052 | 2019 | ก.ย. | 2019-09-23 | 1 | 7.61 | 0.95 | 351.09 | 49 | 2492 | 0.01 | 0 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 0.95
2019-053 | 2019 | ก.ย. | 2019-09-27 | 1 | 7.45 | 0.57 | 210.06 | 23 | 1790 | 0.01 | 0.74 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 0.57
2019-054 | 2019 | ก.ย. | 2019-09-27 | 2 | 7.67 | 0 | 151.49 | 29 | 1760 | 0 | 0.99 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2019-055 | 2019 | ต.ค. | 2019-10-01 | 3 | 8.36 | 0.09 | 158.96 | 42 | 2018 | 0 | 0.72 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 0.09
2019-056 | 2019 | ต.ค. | 2019-10-03 | 1 | 7.76 | 1.43 | 110.21 | 25 | 1614 | 0 | 0.24 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.43
2019-057 | 2019 | ต.ค. | 2019-10-11 | 3 | 8.17 | 1.19 | 221.36 | 51 | 1840 | 0.02 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.19
2019-058 | 2019 | ต.ค. | 2019-10-09 | 2 | 7.86 | 1.5 | 226.21 | 37 | 2048 | 0.02 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.5
2019-059 | 2019 | ต.ค. | 2019-10-17 | 2 | 8.03 | 0 | 164.67 | 37 | 1764 | 0.01 | 1.03 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2019-060 | 2019 | ต.ค. | 2019-10-22 | 3 | 7.48 | 0.93 | 232.98 | 25 | 2426 | 0.01 | 0.19 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.93
2019-061 | 2019 | ต.ค. | 2019-10-25 | 1 | 7.57 | 2.76 | 192.45 | 38 | 2722 | 0.01 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 2.76
2019-062 | 2019 | พ.ย. | 2019-11-04 | 1 | 7.55 | 3.14 | 92.59 | 13 | 1542 | 0 | 1.38 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 3.14
2019-063 | 2019 | พ.ย. | 2019-11-06 | 2 | 7.66 | 1.2 | 153.11 | 23 | 1822 | 0 | 1.43 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 1.2
2019-064 | 2019 | พ.ย. | 2019-11-07 | 3 | 7.92 | 2.93 | 110.85 | 33 | 1576 | 0 | 0.77 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 2.93
2019-065 | 2019 | พ.ย. | 2019-11-12 | 1 | 7.86 | 1.07 | 103.23 | 28 | 1548 | 0.01 | 0.12 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 1.07
2019-066 | 2019 | พ.ย. | 2019-11-21 | 3 | 8.13 | 5 | 75.73 | 15 | 1628 | 0.02 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 5
2019-067 | 2019 | พ.ย. | 2019-11-23 | 1 | 7.83 | 11.84 | 369.85 | 42 | 1914 | 0.01 | 1.2 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 11.84
2019-068 | 2019 | พ.ย. | 2019-11-26 | 1 | 7.85 | 5.82 | 203.7 | 21 | 1448 | 0.01 | 0.46 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 5.82
2019-069 | 2019 | พ.ย. | 2019-11-27 | 2 | 7.93 | 6.68 | 203.7 | 24 | 1494 | 0.01 | 1.57 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 6.68
2019-070 | 2019 | ธ.ค. | 2019-12-02 | 1 | 7.69 | 2.89 | 288.3 | 41 | 2084 | 0 | 0.06 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 2.89
2019-071 | 2019 | ธ.ค. | 2019-12-11 | 1 | 7.79 | 3.5 | 96.54 | 11 | 1066 | 0 | 1.8 | 0 | 0.06 |  |  | 10 | 7.5 |  |  | 3.5
2019-072 | 2019 | ธ.ค. | 2019-12-13 | 3 | 7.86 | 1.17 | 142.3 | 19 | 1082 | 0.01 | 1.28 | 0 | 0.07 |  |  | 10 | 7.5 |  |  | 1.17
2019-073 | 2019 | ธ.ค. | 2019-12-21 | 1 | 7.79 | 0.37 | 78.07 | 28 | 900 | 0 | 0.53 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 0.37
2019-074 | 2019 | ธ.ค. | 2019-12-21 | 2 | 7.73 | 0.35 | 70.06 | 22 | 926 | 0 | 1.6 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 0.35
2020-001 | 2020 | ม.ค. | 2020-01-06 | 3 | 7.44 | 0 | 98.58 | 13 | 974 | 0.02 | 1.48 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0
2020-002 | 2020 | ม.ค. | 2020-01-10 | 2 | 7.82 | 0 | 88.41 | 10 | 1158 | 0 | 1.07 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 0
2020-003 | 2020 | ม.ค. | 2020-01-18 | 1 | 7.38 | 0 | 108.03 | 6 | 856 | 0.01 | 0.64 | 0 | 0.08 |  |  | 10 | 7.5 |  |  | 0
2020-004 | 2020 | ม.ค. | 2020-01-21 | 3 | 7.65 | 0.45 | 89.19 | 11 | 964 | 0.01 | 0.91 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 0.45
2020-005 | 2020 | ม.ค. | 2020-01-24 | 2 | 7.81 | 2.12 | 108.72 | 11 | 1034 | 0 | 1.05 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 2.12
2020-006 | 2020 | ม.ค. | 2020-01-30 | 1 | 7.93 | 1.32 | 123 | 42 | 768 | 0 | 3.05 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 1.32
2020-007 | 2020 | ก.พ. | 2020-02-04 | 2 | 6.71 | 1.21 | 160.42 | 12 | 1304 | 0 | 1.1 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 1.21
2020-008 | 2020 | ก.พ. | 2020-02-06 | 3 | 7.33 | 1.05 | 161.82 | 21 | 1116 | 0 | 0 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 1.05
2020-009 | 2020 | ก.พ. | 2020-02-13 | 1 | 7.01 | 0.87 | 190 | 11 | 944 | 0 | 1.13 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0.87
2020-010 | 2020 | ก.พ. | 2020-02-13 | 3 | 6.71 | 1.78 | 8.71 | 10 | 830 | 0 | 0.78 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 1.78
2020-011 | 2020 | ก.พ. | 2020-02-17 | 2 | 7.1 | 1.65 | 57.24 | 7 | 1142 | 0.01 | 0 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 1.65
2020-012 | 2020 | ก.พ. | 2020-02-20 | 3 | 6.65 | 1.55 | 199.28 | 9 | 906 | 0.01 | 1.25 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 1.55
2020-013 | 2020 | ก.พ. | 2020-02-26 | 1 | 6.2 | 0.94 | 129.63 | 13 | 1024 | 0 | 0.94 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.94
2020-014 | 2020 | ก.พ. | 2020-02-28 | 3 | 7.15 | 1.81 | 615.35 | 27 | 3800 | 0 | 0.01 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 1.81
2020-015 | 2020 | มี.ค. | 2020-03-04 | 1 | 7.51 | 1.6 | 114.76 | 14 | 870 | 0 | 0.76 | 0 | 0.05 |  |  | 10 | 7.5 |  |  | 1.6
2020-016 | 2020 | มี.ค. | 2020-03-05 | 3 | 7.66 | 1.45 | 219.86 | 17 | 1226 | 0 | 0.4 | 0.02 | 0.06 |  |  | 10 | 7.5 |  |  | 1.45
2020-017 | 2020 | มี.ค. | 2020-03-06 | 2 | 8.06 | 0 | 194.66 | 19 | 824 | 0 | 1.44 | 0.02 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2020-018 | 2020 | มี.ค. | 2020-03-10 | 1 | 7.41 | 0.57 | 110.47 | 13 | 758 | 0 | 1.52 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 0.57
2020-019 | 2020 | มี.ค. | 2020-03-13 | 3 | 7.52 | 0 | 110.33 | 28 | 738 | 0 | 0.02 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0
2020-020 | 2020 | มี.ค. | 2020-03-18 | 1 | 7.9 | 1.67 | 50.73 | 13 | 628 | 0 | 0.03 | 0.01 | 0.04 |  |  | 10 | 7.5 |  |  | 1.67
2020-021 | 2020 | มี.ค. | 2020-03-20 | 2 | 8.07 | 1.75 | 361.08 | 28 | 1280 | 0 | 0.02 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 1.75
2020-022 | 2020 | มี.ค. | 2020-03-23 | 3 | 7.68 | 4.75 | 451.67 | 33 | 1696 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 4.75
2020-023 | 2020 | มี.ค. | 2020-03-26 | 1 | 7.63 | 2.66 | 139.8 | 14 | 892 | 0 | 1.42 | 0 | 0 |  |  | 10 | 7.5 |  |  | 2.66
2020-024 | 2020 | มี.ค. | 2020-03-30 | 2 | 7.66 | 3.44 | 218 | 10 | 902 | 0.01 | 1.19 | 0.01 | 0.01 |  |  | 10 | 7.5 |  |  | 3.44
2020-025 | 2020 | เม.ย. | 2020-04-02 | 3 | 7.66 | 3.7 | 278.9 | 11 | 880 | 0 | 0.6 | 0 | 0 |  |  | 10 | 7.5 |  |  | 3.7
2020-026 | 2020 | เม.ย. | 2020-04-08 | 1 | 7.2 | 2.41 | 234.75 | 8 | 882 | 0 | 0.84 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 2.41
2020-027 | 2020 | เม.ย. | 2020-04-15 | 2 | 7.43 | 0.91 | 284.09 | 7 | 1164 | 0.02 | 1.17 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0.91
2020-028 | 2020 | เม.ย. | 2020-04-21 | 3 | 7.37 | 0.8 | 211.13 | 9 | 1006 | 0.02 | 0.44 | 0 | 0.06 |  |  | 10 | 7.5 |  |  | 0.8
2020-029 | 2020 | เม.ย. | 2020-04-22 | 1 | 7.68 | 1.55 | 449.55 | 61 | 1610 | 0.02 | 0 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 1.55
2020-030 | 2020 | เม.ย. | 2020-04-27 | 2 | 7.62 | 0 | 334.23 | 7 | 1096 | 0.03 | 0 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2020-031 | 2020 | เม.ย. | 2020-04-30 | 1 | 8.14 | 0 | 169.66 | 37 | 424 | 0.02 | 0.01 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2020-032 | 2020 | พ.ค. | 2020-05-12 | 1 | 7.6 | 0 | 122.66 | 8 | 1046 | 0.02 | 1.08 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2020-033 | 2020 | พ.ค. | 2020-05-18 | 2 | 7.58 | 1.71 | 147 | 11 | 996 | 0 | 1.24 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 1.71
2020-034 | 2020 | พ.ค. | 2020-05-20 | 3 | 7.86 | 0.21 | 120.94 | 13 | 868 | 0.01 | 0.71 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0.21
2020-035 | 2020 | พ.ค. | 2020-05-28 | 1 | 8.5 | 0.99 | 189.86 | 13 | 1332 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.99
2020-036 | 2020 | มิ.ย. | 2020-06-08 | 3 | 7.85 | 0 | 118.15 | 14 | 700 | 0.03 | 1.98 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2020-037 | 2020 | มิ.ย. | 2020-06-10 | 1 | 7.86 | 0.35 | 592.76 | 16 | 1778 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.35
2020-038 | 2020 | มิ.ย. | 2020-06-11 | 2 | 7.86 | 0.68 | 592.67 | 45 | 1910 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.68
2020-039 | 2020 | มิ.ย. | 2020-06-15 | 3 | 7.95 | 0.63 | 446.27 | 36 | 1700 | 0.05 | 0 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0.63
2020-040 | 2020 | มิ.ย. | 2020-06-16 | 1 | 7.54 | 0 | 372.65 | 19 | 1682 | 0 | 0 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2020-041 | 2020 | มิ.ย. | 2020-06-17 | 3 | 8.35 | 0 | 295.1 | 27 | 1706 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2020-042 | 2020 | มิ.ย. | 2020-06-18 | 2 | 7.75 | 0 | 284.83 | 14 | 1244 | 0 | 0.16 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 0
2020-043 | 2020 | มิ.ย. | 2020-06-23 | 1 | 7.95 | 0 | 164.16 | 20 | 1274 | 0.01 | 0.04 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2020-044 | 2020 | ก.ค. | 2020-07-01 | 2 | 7.48 | 1.54 | 394.58 | 10 | 1522 | 0 | 0 | 0.01 | 0 |  |  | 10 | 7.5 |  |  | 1.54
2020-045 | 2020 | ก.ค. | 2020-07-09 | 3 | 8.04 | 1.4 | 82.24 | 17 | 918 | 0 | 0.14 | 0.01 | 0.16 |  |  | 10 | 7.5 |  |  | 1.4
2020-046 | 2020 | ก.ค. | 2020-07-15 | 1 | 7.69 | 0.99 | 191.53 | 22 | 1338 | 0.25 | 0 | 0 | 0.23 |  |  | 10 | 7.5 |  |  | 0.99
2020-047 | 2020 | ก.ค. | 2020-07-22 | 2 | 7.52 | 0.48 | 150.15 | 7 | 1102 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.48
2020-048 | 2020 | ก.ค. | 2020-07-29 | 1 | 7.77 | 0 | 173.51 | 16 | 1040 | 0 | 1.14 | 0 | 0.05 |  |  | 10 | 7.5 |  |  | 0
2020-049 | 2020 | ส.ค. | 2020-08-03 | 3 | 7.75 | 3.03 | 76.06 | 8 | 828 | 0 | 0.39 | 0.02 | 0.02 |  |  | 10 | 7.5 |  |  | 3.03
2020-050 | 2020 | ส.ค. | 2020-08-05 | 1 | 7.84 | 0 | 172.12 | 13 | 1140 | 0 | 0.39 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0
2020-051 | 2020 | ส.ค. | 2020-08-11 | 2 | 7.7 | 0 | 190.23 | 13 | 1128 | 0 | 0.01 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2020-052 | 2020 | ส.ค. | 2020-08-17 | 3 | 7.73 | 0 | 164.7 | 10 | 936 | 0.1 | 0.65 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 0
2020-053 | 2020 | ส.ค. | 2020-08-24 | 2 | 7.68 | 4.06 | 160.63 | 19 | 1168 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 4.06
2020-054 | 2020 | ส.ค. | 2020-08-24 | 3 | 7.68 | 0 | 140.08 | 18 | 1528 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2020-055 | 2020 | ส.ค. | 2020-08-27 | 1 | 8.53 | 4.04 | 147.35 | 14 | 1402 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 4.04
2020-056 | 2020 | ก.ย. | 2020-09-02 | 2 | 7.71 | 0 | 155.41 | 7 | 964 | 0 | 1.14 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 0
2020-057 | 2020 | ก.ย. | 2020-09-08 | 3 | 7.97 | 0 | 176.2 | 13 | 1150 | 0 | 1.22 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2020-058 | 2020 | ก.ย. | 2020-09-11 | 1 | 7.72 | 0.81 | 69.52 | 13 | 860 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.81
2020-059 | 2020 | ก.ย. | 2020-09-17 | 2 | 7.73 | 0 | 143.63 | 24 | 1040 | 0 | 1.93 | 0 | 0.06 |  |  | 10 | 7.5 |  |  | 0
2020-060 | 2020 | ก.ย. | 2020-09-23 | 3 | 8.28 | 1.4 | 280.46 | 41 | 1680 | 0.01 | 0.03 | 0.01 | 0.02 |  |  | 10 | 7.5 |  |  | 1.4
2020-061 | 2020 | ก.ย. | 2020-09-26 | 1 | 8.17 | 3.53 | 71.28 | 34 | 1220 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 3.53
2020-062 | 2020 | ต.ค. | 2020-10-05 | 2 | 8.04 | 1.02 | 241.79 | 14 | 1366 | 0 | 2.15 | 0 | 0.06 |  |  | 10 | 7.5 |  |  | 1.02
2020-063 | 2020 | ต.ค. | 2020-10-07 | 3 | 8.07 | 1.42 | 288.93 | 17 | 1384 | 0 | 1.39 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 1.42
2020-064 | 2020 | ต.ค. | 2020-10-15 | 1 | 8.14 | 0.72 | 309.84 | 11 | 1684 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.72
2020-065 | 2020 | ต.ค. | 2020-10-15 | 2 | 8.14 | 0.5 | 221.74 | 22 | 1342 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.5
2020-066 | 2020 | ต.ค. | 2020-10-20 | 3 | 8.16 | 0 | 431.22 | 25 | 1844 | 0 | 0 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0
2020-067 | 2020 | ต.ค. | 2020-10-24 | 1 | 7.95 | 0.07 | 297.39 | 27 | 1474 | 0.01 | 0.04 | 0 | 0.05 |  |  | 10 | 7.5 |  |  | 0.07
2020-068 | 2020 | ต.ค. | 2020-10-28 | 2 | 7.99 | 1.69 | 425.06 | 33 | 1638 | 0 | 0.02 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 1.69
2020-069 | 2020 | พ.ย. | 2020-11-04 | 3 | 7.99 | 0 | 232.62 | 19 | 1286 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2020-070 | 2020 | พ.ย. | 2020-11-09 | 1 | 8.15 | 0.98 | 186.69 | 49 | 1166 | 0.02 | 0.04 | 0 | 0.09 |  |  | 10 | 7.5 |  |  | 0.98
2020-071 | 2020 | พ.ย. | 2020-11-12 | 2 | 7.8 | 1.1 | 264.31 | 50 | 1394 | 0 | 0.03 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 1.1
2020-072 | 2020 | พ.ย. | 2020-11-13 | 3 | 8.47 | 1.25 | 427.96 | 58 | 1750 | 0 | 0.03 | 0 | 0.05 |  |  | 10 | 7.5 |  |  | 1.25
2020-073 | 2020 | พ.ย. | 2020-11-18 | 1 | 8.05 | 0.67 | 183.33 | 45 | 1508 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.67
2020-074 | 2020 | พ.ย. | 2020-11-24 | 2 | 8.1 | 2 | 447.7 | 43 | 1924 | 0.01 | 0.07 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 2
2020-075 | 2020 | ธ.ค. | 2020-12-03 | 1 | 7.85 | 1.4 | 359.44 | 29 | 1926 | 0.01 | 0.01 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 1.4
2020-076 | 2020 | ธ.ค. | 2020-12-04 | 2 | 8.03 | 2.98 | 405.58 | 52 | 1924 | 0.01 | 0.04 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 2.98
2020-077 | 2020 | ธ.ค. | 2020-12-07 | 3 | 7.84 | 0.65 | 383.14 | 51 | 1758 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.65
2020-078 | 2020 | ธ.ค. | 2020-12-11 | 1 | 7.84 | 0 | 346.72 | 42 | 2082 | 0.03 | 0.02 | 0 | 0.06 |  |  | 10 | 7.5 |  |  | 0
2020-079 | 2020 | ธ.ค. | 2020-12-22 | 2 | 8.39 | 0.22 | 271.88 | 41 | 1966 | 0 | 0.02 | 0.02 | 0.06 |  |  | 10 | 7.5 |  |  | 0.22
2020-080 | 2020 | ธ.ค. | 2020-12-23 | 3 | 7.82 | 0.32 | 146.25 | 24 | 1278 | 0.02 | 0 | 0.01 | 0.02 |  |  | 10 | 7.5 |  |  | 0.32
2021-001 | 2021 | ม.ค. | 2021-01-05 | 1 | 7.5 | 0.89 | 126.61 | 18 | 1706 | 0 | 0 | 0 | 0.05 |  |  | 10 | 7.5 |  |  | 0.89
2021-002 | 2021 | ม.ค. | 2021-01-11 | 2 | 7.63 | 0.68 | 295.67 | 31 | 1636 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.68
2021-003 | 2021 | ม.ค. | 2021-01-18 | 3 | 7.83 | 0 | 295.97 | 53 | 1736 | 0.03 | 0.14 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 0
2021-004 | 2021 | ม.ค. | 2021-01-18 | 1 | 7.5 | 0.53 | 435.18 | 35 | 1818 | 0.03 | 0.14 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 0.53
2021-005 | 2021 | ม.ค. | 2021-01-23 | 2 | 7.68 | 0.26 | 346.65 | 33 | 1844 | 0 | 0 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0.26
2021-006 | 2021 | ม.ค. | 2021-01-26 | 3 | 7.77 | 0.22 | 183.42 | 39 | 1768 | 0.02 | 0 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0.22
2021-007 | 2021 | ก.พ. | 2021-02-01 | 1 | 7.64 | 1.35 | 207.27 | 17 | 1644 | 0.04 | 0.05 | 0 | 0.06 |  |  | 10 | 7.5 |  |  | 1.35
2021-008 | 2021 | ก.พ. | 2021-02-04 | 2 | 7.68 | 0.83 | 228.76 | 33 | 1552 | 0 | 0 | 0.01 | 0.06 |  |  | 10 | 7.5 |  |  | 0.83
2021-009 | 2021 | ก.พ. | 2021-02-08 | 3 | 7.89 | 0.24 | 197.63 | 28 | 1936 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.24
2021-010 | 2021 | ก.พ. | 2021-02-15 | 1 | 7.58 | 0 | 333.54 | 16 | 1708 | 0.02 | 0 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2021-011 | 2021 | ก.พ. | 2021-02-16 | 2 | 7.76 | 0.48 | 286.67 | 34 | 1400 | 0.2 | 0 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 0.48
2021-012 | 2021 | ก.พ. | 2021-02-19 | 3 | 7.45 | 0.4 | 240.43 | 34 | 1356 | 0.24 | 0.53 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 0.4
2021-013 | 2021 | ก.พ. | 2021-02-23 | 1 | 7.79 | 0 | 377.04 | 26 | 1896 | 0.09 | 0 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2021-014 | 2021 | ก.พ. | 2021-02-27 | 2 | 7.86 | 0 | 354.41 | 25 | 1864 | 0.03 | 0.1 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2021-015 | 2021 | มี.ค. | 2021-03-03 | 3 | 7.72 | 0.65 | 473.7 | 26 | 1944 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.65
2021-016 | 2021 | มี.ค. | 2021-03-03 | 3 | 7.72 | 0.65 | 473.7 | 26 | 1944 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.65
2021-017 | 2021 | มี.ค. | 2021-03-05 | 1 | 8.2 | 0.13 | 346.2 | 21 | 1600 | 0.04 | 0.05 | 0 | 0.05 |  |  | 10 | 7.5 |  |  | 0.13
2021-018 | 2021 | มี.ค. | 2021-03-10 | 2 | 8.24 | 0 | 556.91 | 22 | 2500 | 0.02 | 0 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0
2021-019 | 2021 | มี.ค. | 2021-03-15 | 1 | 8.09 | 0 | 345.03 | 19 | 1784 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2021-020 | 2021 | มี.ค. | 2021-03-15 | 3 | 8.26 | 1.51 | 441.22 | 31 | 1820 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.51
2021-021 | 2021 | มี.ค. | 2021-03-17 | 2 | 8.1 | ND | 333.2 | 19 | 1816 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | ND
2021-022 | 2021 | มี.ค. | 2021-03-22 | 1 | 7.89 | 0.25 | 266.9 | 29 | 1752 | 0.03 | 0.05 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0.25
2021-023 | 2021 | มี.ค. | 2021-03-23 | 3 | 8.05 | 4.36 | 238.41 | 31 | 1744 | 0.03 | 0.03 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 4.36
2021-024 | 2021 | มี.ค. | 2021-03-27 | 2 | 8.29 | 1.81 | 238.81 | 27 | 1884 | 0.04 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.81
2021-025 | 2021 | เม.ย. | 2021-04-01 | 3 | 8.16 | ND | 309.85 | 26 | 2160 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | ND
2021-026 | 2021 | เม.ย. | 2021-04-07 | 1 | 8.02 | 0.95 | 123.66 | 22 | 1356 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.95
2021-027 | 2021 | เม.ย. | 2021-04-10 | 2 | 7.98 | 1.59 | 309.69 | 41 | 1436 | 0 | 0.02 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 1.59
2021-028 | 2021 | เม.ย. | 2021-04-21 | 3 | 7.75 | 0 | 590.72 | 45 | 2376 | 0 | 0.01 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0
2021-029 | 2021 | เม.ย. | 2021-04-22 | 1 | 7.59 | 1.71 | 1067 | 67 | 3228 | 0 | 0.02 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 1.71
2021-030 | 2021 | เม.ย. | 2021-04-24 | 2 | 7.85 | 1.76 | 749.66 | 29 | 2356 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.76
2021-031 | 2021 | เม.ย. | 2021-04-26 | 2 | 7.9 | 0.34 | 703.23 | 29 | 2672 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.34
2021-032 | 2021 | เม.ย. | 2021-04-27 | 3 | 8.18 | 0.8 | 262.31 | 25 | 1404 | 0 | 0.6 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0.8
2021-033 | 2021 | เม.ย. | 2021-04-28 | 2 | 7.77 | 1.28 | 334.66 | 18 | 1524 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.28
2021-034 | 2021 | เม.ย. | 2021-04-30 | 3 | 8.05 | 1.98 | 203.42 | 25 | 1208 | 0 | 1.24 | 0 | 0.02 |  |  | 10 | 7.5 |  |  | 1.98
2021-035 | 2021 | พ.ค. | 2021-05-03 | 1 | 7.91 | 1.23 | 240.11 | 36 | 1388 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.23
2021-036 | 2021 | พ.ค. | 2021-05-03 | 2 | 8.05 | 0 | 180.66 | 18 | 1288 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
2021-037 | 2021 | พ.ค. | 2021-05-07 | 3 | 8.02 | 0 | 172.72 | 36 | 1520 | 0.01 | 0 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 0
2021-038 | 2021 | พ.ค. | 2021-05-08 | 1 | 8.23 | 0 | 254.91 | 24 | 1312 | 0.02 | 0 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 0
2021-039 | 2021 | พ.ค. | 2021-05-12 | 2 | 7.92 | 0.1 | 670.86 | 40 | 2248 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.1
2021-040 | 2021 | พ.ค. | 2021-05-14 | 2 | 7.96 | 1.84 | 492.61 | 25 | 1848 | 0.01 | 0.93 | 0 | 0.03 |  |  | 10 | 7.5 |  |  | 1.84
2021-041 | 2021 | พ.ค. | 2021-05-14 | 3 | 8.31 | 4.02 | 204.78 | 28 | 1252 | 0.01 | 1 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 4.02
2021-042 | 2021 | พ.ค. | 2021-05-18 | 1 | 8.3 | 2.33 | 397.62 | 32 | 1948 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 2.33
2021-043 | 2021 | พ.ค. | 2021-05-21 | 2 | 8.23 | 0.09 | 461.1 | 38 | 1840 | 0.02 | 0.69 | 0 | 0.04 |  |  | 10 | 7.5 |  |  | 0.09
2021-044 | 2021 | พ.ค. | 2021-05-28 | 3 | 8.34 | 1.09 | 336.09 | 27 | 1860 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.09
2021-045 | 2021 | พ.ค. | 2021-05-31 | 1 | 8.11 | 0.27 | 461.41 | 34 | 1808 | 0 | 0 | 0 | 0.01 |  |  | 10 | 7.5 |  |  | 0.27
2021-046 | 2021 | มิ.ย. | 2021-06-05 | 2 | 8.36 | 0 | 232.12 | 40 | 1340 | 0.03 | 0.06 | 0.01 | 0.02 |  |  | 10 | 7.5 |  |  | 0
2021-047 | 2021 | มิ.ย. | 2021-06-12 | 3 | 8.23 | 0.54 | 429.84 | 30 | 1756 | 0.02 | 0.03 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0.54
2021-048 | 2021 | มิ.ย. | 2021-06-16 | 1 | 8.39 | 1.77 | 317.94 | 46 | 1660 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 1.77
2021-049 | 2021 | มิ.ย. | 2021-06-21 | 2 | 8.02 | 0 | 752.8 | 36 | 2692 | 0 | 0 | 0 | 0 |  |  | 10 | 7.5 |  |  | 0
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
[16 empty] | 10 | 7.5 |  |  | #VALUE!
This shape represents a table slicer. Table slicers are supported in Excel or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
Report Graph